## All Systems Except Tribes
Agency Characteristics | [32 empty] | Community Characteristics | [5 empty] | Drinking Water | [9 empty] | Regulatory Issues | [5 empty] | Wastewater |  |  | Stormwater |  | Affordability
2017/18 Survey Response | 2014 Survey Response | Count | Water/ Wastewater System |  |  | System has paid FT staff (y/n) | System has identified itself as in need of financial assistance (y/n) | System has a current Emergency Response Plan (y/n) | # Hookups | Rate structure described | Involvement with NCRP categories | Has Submitted Project to NCRP | Level of concern for system on the following topics (0 = no concern, 1 = moderate, 2 = strong, 3 = extreme, N/A = N/A "blank" = no response): | [11 empty] | Level of need for technical assistance (0 = no concern, 1 = moderate, 2 = strong, 3 = extreme, N/A = N/A "blank" = no response): | [17 empty] | Average Monthly Bill (either water, wastewater, or both) | [16 empty] | EPA Affordability Criteria Threshold
|  |  |  | Type | Address | [7 empty] | Water Quality - raw | Drinking water supply reliability | Fire suppression supply reliability | Water pressure issues | Outdated treatment system | Aging treatment system | Sufficient quality and quantity of staff | System too small; population increasing | System too large; population decreasing | Financial stability for operating system and maintaining reserve | Operation and maintenance – need for trained personnel | Meeting current regulations | System infrastructure - operations | System infrastructure - maintenance and repair | Equipment calibration | Administration | Capital Improvement Planning | Rate Structures | Funding Opportunities | Meeting Current Regulations | Community | County | IRWM region | Median Household Income (MHI) | Tribal Community (y/n) | Population | Primary source of water | Specifics about water source(s) | Estimate number of private wells | Estimate number of public wells |  | Monthly Bill Categories | Water Treatment Information | Drinking water system issues & system status | Drinking Water System Status Categories | Anything (other than AS) unusual or problematic about water source? | DDW Rank | DDW Violation Type | DDW Action Date | SWRCB Rank | RWQCB Decision Type | RWQCB Date | Type of system | Describe any insufficient wastewater system issues & system status | Sewer System Issue Categories | Identify stormwater/ urban water runoff/ flood management issues | Water > 2.5% | WW > 2% | Both > 4.5%
|  | 1 | AIRPORT/LARKFIELD/WIKIUP SANITATION ZONE (ALWSZ) | Public Utility | Airport, Larkfield Wikiup area of Santa Rosa | y | n |  | 3639 |  | Familiar; regular participant | [21 empty] | Larkfield, Wikiup | Sonoma | North Coast, Region 1 | 46037 | N | 8884 | [16 empty] | sewer | The neighborhood of Larkfield Estates, which was heavily impacted by the October 2017 Sonoma Complex Fires, lies within the boundary of the Airport/Larkfield/Wikiup Sanitation Zone (ALWSZ) and is therefore eligible to connect to sewer service. As the neighborhood rebuilds, property owners may be interested in pursuing sewer connection for their properties. In order to connect homes in Larkfield Estates to the ALWSZ, a sewer collection system needs to be designed and built, and property owners would need to pay the ALWSZ connection fee. After being approached by property owners in Larkfield Estates, Sonoma Water has developed a program to extend sewer service to the neighborhood for voluntary connection as well as a financing program for property owners interested in connecting to sewer. Participation in the sewer project is entirely voluntary. Signup Deadline Extended - On Febrary 5, 2019, the Board of Directors of Sonoma Water approved the Larkfield Estates Sewer project, which will bring sewer service to willing property owners in Larkfield Estates. The deadline to sign up for the project has been extended to September 16, 2019. | Interest/ plan to consolidate
y |  | 1 | ALBION MUTUAL WATER COMPANY | Mutual | PO Box 485, Albion, CA 95410 | n | y | y | 27 | seasonal | Unfamiliar; interested |  | 1 | 1 | 2 | 0 | 0 | 2 | n/a | n/a | n/a | 1 | N/A | 0 | 1 | 0 | 0 | 1 | 0 |  | 2 |  | Albion Village | Mendocino | North Coast, Region 1 | 39667 | n | 40 | GW | Wells (2) |  | 2 | Average service fees range between $41 and $60 per month. | $51 - $100 |  | The Company has two active wells (East and West Wells) and owns and/or maintains approximately 0.8 miles of pipeline and no additional infrastructure. | Good condition | no
| y | 1 | ALDERPOINT COUNTY WATER | Water Dist | P.O. Box 117 ALDERPOINT, CA 95511 | n | y |  | 79 | uniform rate schedule | Familiar; infrequent participation | Unfunded | [13 empty] | 1 |  | 1 | 1 |  | 1 |  | Alderpoint | Humboldt | North Coast, Region 1 | 26813 | n | 219 | SW | IN - Eel River - untreated |  |  | 0-50; minimum monthly fee of $40.00 for first 2,000. cu. ft. after that additional usage will be billed according to use at same rate per cubic foot. | $0 - $50 | Calcium hypochlorite, a disinfectant, is added to the water in the 5,000-gallon tank. From the 5,000-gallon staging/preliminary distribution tank, water is pumped up another 300-feet, via a six inch main, to a 100,000-gallon redwood storage tank. This main storage tank feeds water into the distribution system serving the community. The source of water for the District is an infiltration gallery in the Eel River bed. The infiltration gallery collection pipe is approximately nine feet below the bed of the river. From the infiltration gallery wet well, water is pumped through a six-inch cast iron main to a 5,000-gallon staging tank located 130 feet above the riverbed. The 5,000-gallon tank and its accompanying pump house are located just off River Road. Calcium hypochlorite, a disinfectant, is added to the water in the 5,000-gallon tank. From the 5,000-gallon staging/preliminary distribution tank, water is pumped up another 300-feet, via a six inch main, to a 100,000-gallon redwood storage tank. This main storage tank feeds water into the distribution system serving the community. The Alderpoint CWD recently installed a water filtration system to bring the water quality into compliance with State of California regulations. In 2014, Alderpoint CWD replaced a leaking 100,000-gallon redwood tank with a new 160,000-gallon steel tank, which reduced the amount of water withdrawn from the Eel River by at least 50 percent. |  |  | no | A | 1. Violation of MCL for total coliform bacteria 2. Failure to submit monthly monitoring reports 3. Violation of Section 116555 pf the CA Health and Safety Code, which requires each public water system to have a reliable supply of water to serve its customers | 1. 4/26/2017 2. 10/8/15 3. 10/17/14
|  | 1 | ALEXANDER VALLEY ACRES WATER COMPANY | Other | Sonoma County | [28 empty] | Sonoma |  | 57639 | n | 30
| y | 1 | ANCIENT REDWOODS R.V. PARK PWS #120 6011 | other | Humboldt | y | n |  | 25-50 | contained in rental fees | [22 empty] | Ancient Redwoods RV Park | Humboldt | North Coast, Region 1 | 48542 | n | 50-100
|  | 1 | Anderson Valley Community Services District | CSD | [29 empty] | Mendocino | North Coast, Region 1 | 36932 | n | 1035 |  |  | > 23 |  |  |  |  | We are currently in the planning process which consists of a feasibility study that establishes a proposed service area, identifies options to develop public utility service (water or wastewater) within it, evaluates the options with respect to cost, environmental impacts and acceptability to the community, and concludes with a recommended project description. The recommended project will then be presented to the community for comment and, after receipt of public input, modified as directed by the District. Based on community support, the District will then determine whether to move forward to seek financing for implementation of the project including proceeding with the establishment of local mechanisms (rates, assessments, etc.) that would ultimately be needed to repay possible project loans and fund system operations and maintenance. Phone call with Joyce Andrews (General Manager), 1.9.20: proposal to build wwtp and water supply facilities will be presented to rate payers for decision mid-2020. The water proposal is moving forward well - the district is in discussion with several property owners with good water quality and flow to their wells to construct many small wells that will feed into a few treatment facilities. A recent fire in Boonville underscored the need for fire suppression capability - the new water system will be required to include fire suppression tanks. There is more resistance to the wastewater treatment plant with respect to siting. Although it will use MBR technology, which is odorless, soil percolation and neighbor (NIMBY) constraints are making it difficult to find a site. Within the next several months, the district will decide whether to separate the projects and if they do, they will need to redo CEQA. Projects are expected to be fully funded through the state. | Fair condition/ Upgrades planned | [7 empty] | septic | There is historical evidence of private well contamination in Boonville that is most likely attributable to the proximity of wells and onsite septic systems. The presence of small lots in portions of the community exacerbate the problem. Also, many septic systems are nearing the end of their useful life and in some circumstances there is insufficient space for a standard replacement leach field. When a system fails, the only viable alternatives are in these circumstances very expensive. In 2016, water quality testing of samples drawn from 23 wells in the densest housing areas revealed alarming levels of E Coli and nitrates confirming a health issue exists. Funding is currently available under State Proposition 1 to create municipal utility systems. This is a relatively new program and this is an opportunity to take advantage of it. The District is interested in developing utility systems under Proposition 1 programs that provide for planning grants to eligible communities to help make projects affordable. | Regulatory - septic
|  | 1 | ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | Public Utility | 1720 NORTH FIRST STREET SAN JOSE, CA 95112 |  |  |  | 377 | [24 empty] | Sonoma | North Coast, Region 1 | 45489 | n | 420 | GW | Wells (2) |  | 2
|  | 1 | ATHENA TERRACE MUTUAL WATER COMPANY | Other | Sonoma County | [28 empty] | Sonoma |  | 46037 | n
|  | 1 | AUSTIN ACRES MUTUAL WATER COMPANY | Mutual | Sonoma County | [28 empty] | Sonoma |  | 58333 | n
|  | 1 | Austin Creek Mutual (Springhill) | Mutual | P.O. BOX 86 CAZADERO,CA 95421 |  |  |  | 63 | [24 empty] | Sonoma | North Coast, Region 1 | 41389 | n | 150 | GU | Wells (2) |  | 2
|  | 1 | AZALEA GLEN | Other | Humboldt | [28 empty] | Humboldt |  | 50417 | n
| y | 1 | BAR 717 RANCH, INC. (SUMMER CAMP) | Other | Humboldt | y | y |  | 25-50 | no charge | [11 empty] | 1 |  | 1 | 1 | 1 |  |  |  |  | 1 |  | Bar 717 Ranch and summer guests | Humboldt |  | 50417 | n | 100-250
|  | 1 | BEACH CREEK MH PARK | other | 4203 Lowell Ave., La Crescenta, CA 91214 | [28 empty] | Humboldt | North Coast, Region 1 | 20346 | n
|  | 1 | BELMONT TERRACE MUTUAL WATER COMPANY | Mutual | 881 Dorthel Street SEBASTOPOL, CA 95472 |  |  |  | 87 | [24 empty] | Sonoma | North Coast, Region 1 | 99141 | n | 244 | GW | Wells (2) |  | 2
|  | 1 | BENBOW W.C. | Public Utility | Public Utility |  |  |  | 135 | [24 empty] | Humboldt | North Coast, Region 1 | 36371 | n | 150 | SW | IN- East Branch, South Fork Eel | [5 empty] | The Benbow Water Company diverts water from the East Branch of South Fork Eel River through an infiltration gallery located within the river bed. The Benbow Water Company produced approximately 31 million gallons of drinking water in 2005 (2006 California Department of Public Health, now the State Water Resources Control Board Division of Drinking Water (DDW), Annual Inspection Report). Source capacity was identified as a serious problem for this system and pumping capacity was less than maximum day capacity (Winzler and Kelly, 2008, Page 6-91). The Benbow Water Company completed a project to increase filter capacity by installing an additional filter bank. The original filters had a surface area of 39 sq. ft., and were increased to a total surface area of 78 sq. ft. (Personal communication, Troy Hubner, Del Oro Water Company, February 8, 2017). The Benbow Water Company reports that it is operating at approximately 40 percent of its claimed water right (Personal Communication, Winston Benbow, 2010), and is planning to accommodate an additional 20 to 50 new water connections in the next 20 years. | Uncertain water supply |  | 0 | 1. Failure to Monitor for coliform. | 1. 3/7/2013
|  | 1 | BENNETT RIDGE MUTUAL WATER COMPANY | Mutual | Sonoma County | [28 empty] | Sonoma |  | 46037 | n
| y | 1 | BERTSCH OCEANVIEW CSD | CSD | 377 J STREET CRESCENT CITY, CA 95531 | n | n |  | 629 | They contract with Crescent City, which sells water to individuals, and the Bertsch Oceanview CSD charges a water service fee on top of that, for maintenance of the system. | Familiar; not a participant | [21 empty] | Some unincorporated areas of Del Norte County. | Del Norte | North Coast, Region 1 | 26544 | n | 1600 | GWP | CC Smith River Purchased Water - treated XCLD |  |  | $0-50; Bertsch Ocreanview's monthly service fee: $9.75. They contract with Crescent City, which sells water for a minimum monthly cost of $12.30 for 0-500 cubic feet, plus $1.07 for each additional cubic foot. | $0 - $50 |  | The BOV CSD receives its water from the City of Crescent City. From the City’s distribution center, water is conveyed south, through a 12-inch diameter BOVCSD waterline, until it reaches a booster station located on Elk Valley Road.The booster station contains two pumps with sufficient generator backup power for simultaneous operation. Each pump can deliver approximately 550 gallons per minute (GPM) and together, approximately 900 GPM. Typically, a single pump is operated daily for 7-9 hours (depending on the season). The backup power generator has enough electrical capacity and fuel to continuously operate both pumps for a minimum of 24 hours. The distribution system that is upstream of the booster station is considered the BOVCSD water distribution system. The District notes that there are a few BOVCSD connections located downstream of the booster station as well. The BOV CSDwater distribution system contains approximately 12.8 miles of 4-inch-12-inch piping, the majority of which (74%)is 6-inches and 8-inches in diameter. The majority of the BOVCSD’s existing water distribution system was constructed in 1973 and is predominately Asbestos Cement Pipe.The District maintains a 750,000 gallon reservoir that was constructed in 1998. In general, the BOV CSD’s water distribution system has few known deficiencies. The BOV CSDmaintains a master water meter within the booster station and the volume is recorded by Crescent City personnel on a daily basis. The following calculations for the maximum daily demand (MDD) were based on the highest “normalized” data readings. The 2008 normalized MDD was 418,000 gallons. Of the District’s 750,000 gallon reservoircapacity, 300,000 gallons are maintained for fire flows. The remaining 450,000 gallons are available for the District’s useto deliver to its customers. The District reports that there is sufficient capacity within the existing reservoir to maintain the MDD of the BOVCSD without having to utilize the booster station’s available pumping capacity | Good condition
y | y | 1 | BIG LAGOON CSD | CSD | P.O. Box 847 TRINIDAD, CA 95570 | y | n | y | 40 | monthly, annual flat rate | Familiar; infrequent participation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | Big Lagoon | Humboldt | North Coast, Region 1 | 50417 | n | 109 | GW | Wells (2) |  | 2 | 51-100 | $51 - $100 |  | The water system now consists of 2 wells, a 20,000 gallon redwood storage tank, booster pumps and 3,000 gallon hydro pneumatic tank with an air compressor. In 2016, the Chairperson of the CSD Board reported that the system has an “untested theoretical limit of 30,000 gallons per day, if the well runs constantly. This is different from the 70,000 gallons reported (by the Community Infrastructure and Services Technical Report).” (Personal Communication with Valen Castellano, Big Lagoon CSD, April 29, 2016). The system operates with only 10,000 gallons of storage. The Chairperson further stated, “The BLCSD has discussed more water storage, but we are a long way away from realizing the project. Many believe we are at capacity now and could only service one or at most, two new connections. We will review and consider each individual proposal on its particular merits. Further development inland would require serious study and possible expansion of our service area beyond our current 23 acres. An Engineering Study must be done on our current system before we could competently evaluate our current conditions and any room for expanding services.” (Personal Communication with Valen Castellano, Big Lagoon CSD, April 29, 2016) | Uncertain water supply | [7 empty] | sewer
y | y | 1 | BIG LAGOON PARK WATER CO. | other | P.O. BOX 654 EUREKA, CA 95501 | y | n | y | 76 | monthly/ annual flat rate | Unfamiliar; disinterested |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | Big Lagoon Park | Humboldt | North Coast, Region 1 | 20346 | n | 70 | GW | Wells (2) |  | 2 | 0-50 | $0 - $50
|  | 1 | BIG RIVER VISTA MUTUAL WATER COMPANY | Mutual | PO Box 708, Mendocino, CA 95460 | n |  |  | 19 |  | Unfamiliar; disinterested | [21 empty] | Big River area near Mendocino, CA | Mendocino | North Coast, Region 1 | 51277 | n | 36 | GW | Well |  | 1 | Average service fees range between $81 and $100 per month. | $51 - $100 |  | The Company owns and maintains one active well and approximately two miles of pipeline. In addition, the Company owns a well pump, water storage tank and pump, tank liner, treatment building, water treatment equipment, distribution valves, customer meters, and three standpipe hydrants. | Good condition
y | y | 1 | BIG ROCK C.S.D. | CSD | P.O. BOX 453 CRESCENT CITY, CA 95531 | y | y | y | 107 | Increasing block (graduated) rate schedule | Familiar; regular participant |  | 0 | 3 | 0 | 0 | 3 | 3 | 1 | 0 | 0 | 3 | 1 | 0 | 3 | 3 | 1 | 0 | 2 | 3 | 3 |  | Township of Hiouchi | Del Norte | North Coast, Region 1 | 26544 | n | 400 | GW | Well |  | 1 | 51-100 | $51 - $100 |  | The Big Rock CSD collects its water from a single well located adjacent to the Smith River. The District’s total storage capacity is 150,000 gallons, including one 100,000-gallon Redwood tank and one 50,000-gallon Redwood tank. The Big Rock CSD replaced its two submersed river pumps in October 2008 and was reclassified as a groundwater system. Because the pumps’ operating schedules are alternated, they should not have to be replaced for another 13 years. In July 2009, the Big Rock CSD added a newer small pump at the large storage tank (used to push water further uphill into the 50,000-gallon tank) due to the existing primary pump’s mature age. (LAFCO 2015) | Adequate | [7 empty] | septic |  |  |  | 1
y | y | 1 | BLUE LAKE, CITY OF | City | P.O. BOX 458 BLUE LAKE, CA 95525 | y | y | y | 699 | monthly/ annual flate rate | Familiar; infrequent participation | Unfunded | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 2 |  | Blue Lake, CA | Humboldt | North Coast, Region 1 | 49828 | n | 1252 | GWP | Purchases treated from HBMWD |  |  | 51-100 | $51 - $100 | We don't treat; we provide pre-treated water to our customers. | The City’s receives its water supply through contract with HBMWD. Water is delivered through distribution mains and storage reservoirs located throughout the community. The City has approximately 0.9 MG of storage capacity spread over two redwood tanks ranging in size from 400,000 gallons to 500,000 gallons. | Adequate | [8 empty] | The Glendale area receives wastewater service from the Fieldbrook-Glendale CSD. Glendale’s wastewater system is in very good condition overall and has approximately 166 connections. Flows currently range between 37,000 gpd during dry weather and 75,000 gpd during wet weather. The District has a contract to pump raw wastewater to the City of Arcata for treatment and disposal. The existing contract allows for up to 71,200 gpd average dry weather flow, indicating that the system has the capacity for approximately 80 to 100 more connections. Alternative solutions to treatment and disposal must be found toaccommodate any development in excess of this. The City of Arcata has indicated it is not interested at this time in increasing the District’s contract amount and has recommended the District consider other alternatives. The District has approached the City of Blue Lake and will participate in other related studies to evaluate alternatives and costs for potential interconnection. | Good condition
|  | 1 | BLUE SPRUCE MOBILE HOME PARK | other | 7420 Greenhaven Drive - Suite 125 SACRAMENTO, CA 95831 |  |  |  | 56 | [24 empty] | Sonoma | North Coast, Region 1 | 64612 | n | 90 | GW | Well |  | 1
|  | 1 | BODEGA BAY PUBLIC UTILITY DISTRICT | PUD | Sonoma County | [28 empty] | Sonoma |  | 85526 | n
|  | 1 | BODEGA WATER COMPANY | other | P.O. Box 87 BODEGA, CA 94922 |  |  |  | 38 | [24 empty] | Sonoma | North Coast, Region 1 | 85526 | n | 77 | GU | Wells (3) |  | 3 | [6 empty] | A | 1. Fluoride MCL Violation for fourth quarter 2014 2. Total coliform MCL violation for February 2015 3. Disinfection byproducts MCL violations for third quarter 2015 | 1. 3/25/15 2. 4/17/15 3. 11/12/15
|  | 1 | BRAND WATER COMPANY | Other | Sonoma County | [28 empty] | Sonoma |  | 46037 | n
|  | 1 | BRANGER MUTUAL WATER COMPANY, INC. | Other | Sonoma County | [28 empty] | Sonoma |  | 46037 | n
|  | 1 | Branscomb Mutual Water Company | Mutual | 13270 Kenny Creek Road, Branscomb, CA 95417 P.O. BOX 72 BRANSCOMB BRANSCOMB, CA 95417 | n |  |  | 23 | [23 empty] | Branscomb | Mendocino | North Coast, Region 1 | 32667 | n | 92 | SW | IN - GP Spring - Surface water |  |  | Average service fees range between $61 and $80 per month. | $51 - $100 |  |  |  | The Safe Drinking Water Information System lists a number of monitoring violations, dated as recently as September 2017 with compliance achieved March 11, 2018. The United States Environmental Protection Agency (USEPA) notes a monitoring and reporting violation dated January 2009 with compliance achieved in April 2010.6 | 0 | 1. Bacteriological monitoring violation 2. Chemical monitoring violation 3. Citation for NonCompliance | 1. 9/11/17 2. 11/30/17 3. 8/31 17
y |  | 1 | BRICELAND C.S.D. | CSD | P.O. Box 670 REDWAY, CA 95560 | n | y | y | 26 | monthly/ annual flat rate | Familiar; infrequent participation | Funded | 0 | 2 | 2 | 0 | 0 | 3 | 1 | 3 | 0 | 3 | 1 | 0 | 2 | 2 | 0 | 0 | 1 | 1 | 1 |  | Briceland | Humboldt | North Coast, Region 1 | 37778 | n | [5 empty] | 0-50 | $0 - $50 | The Briceland CSD anticipates installing a new roughing filter and a solar powered hypo chlorination unit in the near future. | high rainfall turbidity; The District currently serves 26 lots in the District and 1 outside District boundaries. District representatives have indicated that: “Due to regulatory constraints, the District has no plans of expansion either in terms of size or number of service connections. There are presently four applications for service, the oldest of which has been held on file for more that ten years. The District was formed for the purposes of improving the water system that was supplying water to houses in the Briceland area. The water system that was in place at the time was an antiquated system put in by the original settlers in the 1880’s. The Briceland CSD water system is in poor condition, source capacity is unable to meet current maximum day demands, the treatment system is unable to meet turbidity performance standards during winter months, and storage capacity is barely able to meet even one day of maximum day demands. Briceland is currently operating under a moratorium for new connections. There are currently at least four homes within the District that have submitted requests for service connections; the oldest request is over 16 years old. The Briceland CSD anticipates installing a new roughing filter and a solar powered hypo chlorination unit in the near future. | Poor condition | [7 empty] | septic
| y | 1 | BROOKTRAILS TOWNSHIP CSD | CSD | 3800 Chinquapin Drive WILLITS, CA 95490 |  |  |  | 1554 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Mendocino | North Coast, Region 1 | 32667 | n | 3800 | SW | Instream | [5 empty] | The Districtowns, operates, and maintains a public water system forwater supply, treatment, and distribution. The District’s water system facilities and infrastructure includes two reservoirs, Lake Emily which feeds into Lake Ada Rose,on Willits Creek and a tributary within the Eel River watershed, aWater Treatment Plant (WTP) with adesign capacity of 1.2 million gallons per day (MGD), 24 water tanks with 1.7 million gallons(MG)of storage capacity, 18 pump stations, and 64 miles ofwater mains. The District also has a four-bay utility department garage located at the WTP.The District’s water system is classified as a Large Water System because it has more than 500 connections and is under the jurisdiction of the State Water Resources Control Board (SWRCB) Division of Drinking Water Supply Permit No. CA2310009.The District’s water system serves a total of 1,555 connections, including 1,505 in Brooktrails Township, 49 connections in Spring Creek, and 1 connection to the City of Willits for the Willits Municipal Airport.The District’s water system serves 1,548 residential, 4 commercial, and 3 public service connections.Lake Emily has a physical storage capacity of 251acre-feet (AF),and allowed water rights of 300 AF underSWRCB Water RightPermit No. 015913,and Lake Ada Rose has a storage capacity of 138 AFunderSWRCB Water RightPermit No. 014218, for a total available waterstoragesupplyfor the Districtof 389AF.(BTCSD:2018, 2019; LAFCo, 2010). | Good condition |  | C | 1. Compliance order for violation of section 116555 of CA Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 10/17/14
|  | 1 | BROOKWOOD MOBILE HOME PARK | Other | Sonoma County | [28 empty] | Sonoma |  | 46037 | n
|  | 1 | BUCHER WATER COMPANY | other | [29 empty] | Sonoma |  | 57639 | n
|  | 1 | BUCKTAIL MUTUAL WATER COMPANY | Mutual | P.O. BOX 243 LEWISTON, CA 96052 | n | n |  | 32 | monthly/annual flate rate | Unfamiliar; disinterested | [21 empty] | Bucktail (a community within Lewiston), Trinity County. | Trinity | North Coast, Region 1 | 30000 | n | 51 | GW | Wells (3) |  | 3 | Annual rate: $368/12 = $30.67 | $0 - $50
|  | 1 | BUD FINE MWC | Mutual | [29 empty] | Trinity | North Coast, Region 1 | 30000 | n
y | y | 1 | BURNT RANCH ESTATES Mutual Water Co. | Mutual | PO Box 102 Burnt Ranch, CA 95527 | y | y | no | 35 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 3 |  | Burnt Ranch Estates, 35 households on Pony Express Way, Horseshoe Lane, and Stagecoach Road in Burnt Ranch | Trinity | North Coast, Region 1 | 39167 | n | 115 | SW | IN - McDonald Creek - raw |  |  | 0-50 | $0 - $50 | [10 empty] | septic
y |  | 1 | BUTTE MOBILE HOME PARK | other - mobile home park | 1010 BUTTE ST., CRESCENT CITY, CA 95531 | y | y | no | 23 | monthly/ annual flat rate | Unfamiliar; interested |  | 2 | 2 | 2 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 2 | 0 | 3 |  | Butte Mobile Home Park | Del Norte | North Coast, Region 1 | 26544 | n | 67 | GW | Well (1) |  | 1 | 0-50 | $0 - $50
y |  | 1 | CAL ORE MOBILE ESTATES | mobile home park | 1490 Kellogg Dr, Weed, CA 96094; and (2) Abrams Lake Mobile Estates, 2601 N Old Stage Rd, Mt Shasta, CA 96067 | y | n | y | 52 | monthly/ annual flat rate | Unfamiliar; disinterested |  | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 3 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 2 |  | Cal Ore Mobile Estates | Siskiyou | North Coast, Region 1 | 34000 | n | 146 | GW | SP (1) | [8 empty] | A | 1. Violation of Total Coliform MCL | 1. 8/23/17
|  | 1 | California American GEYSERVILLE WATER WORKS (PUC) | Public Utility | P.O. Box 65 GEYSERVILLE, CA 95441 |  |  |  | 308 | [24 empty] | Sonoma | North Coast, Region 1 | 46250 | n | 875 | GW | Wells (3) |  | 3
| y | 1 | Green Diamond Resource Company - Korbel | Other | Humboldt | n | y |  | 0 - 25 |  | Unfamiliar; interested | [14 empty] | 1 |  |  | 1 |  | 1 | 1 | Mill Site, Humboldt | Humboldt | North Coast, Region 1 | 38816 | n | 0 - 25 |  |  |  |  | private system
|  | 1 | CALIFORNIA-AMERICAN WATER LARKFIELD (PUC) | Public Utility | wikiup |  |  |  | 1803 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 5369 | GW | Water Purchases from SCWA; Wells ((5)
y | y | 1 | CALLAHAN WATER DISTRICT | Water Dist | P.O. Box 1524/820 McKeen Rd. CALLAHAN, CA 96014 | y | y | no | 34 | monthly/ annual flat rate | Familiar; regular participant |  | 2 | 2 | 3 |  | 3 | 3 | 2 | 2 | n/a | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 | 1 | 3 |  | Callahan, CA | Siskiyou | North Coast, Region 1 | 44242 | n | 70 | SW | Instream - West Boulder Creek - Raw |  |  | 0-50 | $0 - $50 |  |  |  |  | C | 1. Failure to monitor for coliform 2. Violation of section 116555 of the CA Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 4/12/13 2. 10/17/14 |  |  |  | septic
y |  | 1 | CALPELLA COUNTY WATER DISTRICT | Water Dist | 151 Laws Avenue UKIAH, CA 95482 | no response | no | y | 176 | uniform rate schedule | Familiar; infrequent participation |  |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Calpella, CA | Mendocino | North Coast, Region 1 | 19356 | n | 730 | Purchase | purchase treated water from Millview CWD and Redwood Valley CWD, also has a Well |  | 1 | 100-150 | $101 - $150 |  | The average normal year demand is 119 AF. The CCWD operates one well with a capacity of 40 AF and in order to meet demand must contract with RRFC for the remainder. Because of geographical constraints, the CCWD must contract with Millview County Water District for treatment and transport. Because of the uncertainty in water supply, the CCWD is under a new hookup moratorium. The Ukiah Valley Special Districts Municipal Service Review of 2013 recommended that Willow CWD, Calpella CWD, and Hopland PUD consider a formal consolidations through LAFCO. | Uncertain water supply | [7 empty] | sewer | [5 empty] | 1
| y | 1 | CAMP LIAHONA REDWOODS (YOUTH SUMMER CAMP) | Other |  | n |  |  | 0-25 |  | Unfamiliar; disinterested | [12 empty] | 1 |  | 1 | [6 empty] | Youth Camp, Sonoma County | Sonoma | North Coast, Region 1 | 39614 | n | 100-150 |  |  |  |  | N/A, summer camp
|  | 1 | CAMP MEEKER WATER SYSTEM | Other | [29 empty] | Sonoma |  | 70714 | n
| y | 1 | CAMP ROYANEH | Other |  |  |  |  | 16 | [23 empty] | Private | Sonoma | North Coast, Region 1 | 49886 | n
|  | 1 | CANON MANOR WATER SYSTEM | Other | [29 empty] | Sonoma |  | 46037 | n
y |  | 1 | CASPAR SOUTH SERVICE COMPANY | other | PO Box 744, Mendocino, CA 95460 | n | y | y | Water:42 connections Sewage: 32 connections to community septic system; 10 individual systems | Flat rate + variable usage charge | Familiar; not a participant | Unfunded | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | South Caspar, CA | Mendocino | North Coast, Region 1 | 46037 | n | 188 | GW | Wells (8) |  | 8 | 100-150 | $101 - $150 |  | shallow wells | Uncertain water supply | [7 empty] | septic | Existing on-site community septic disposal system is inadequate; alternatives are being investigated using a Clean Water Program facilities planning grant The CSWD wastewater system was constructed in the early 1960’s as part of the subdivision’s initial development. The system consists of gravity fed connection laterals, collection tanks, screen separators, and a force main-fed leach field. District-owned treatment facilities were updated in 1982. These improvements consisted of a pumping station and installation of one large community leach field. At that time, the treatment plant located at the end of Otter Point Circle was de-commissioned, and subsequently served as a sewage collection tank. The District works to ensure the integrity of its system via testing and other measures including continual maintenance and monitoring, video camera inspection of lines, and locating and eliminating ‘wet areas’ where leaks are present . Through a series of ‘mini-projects’ (average cost of $15,000), the District is replacing worn-out lines. The most recent mini-project was replacing a 300-foot section of pipe in the southerly portion of the District. The District is also working to identify storm water intrusion sources. Through another series of small projects, the District has been working toward eliminating the intrusion problem. The District has also installed backflow prevention devices in each residential lateral, and has added two generators at each pump station in case of a power outage. Currently, the District is making system improvements including replacing aged pipes. CSWD has noted that its existing facilities are sufficiently sized to accommodate a total of 75 residential dwelling units. | Fair condition/ Upgrades planned/ identified |  | 1
|  | 1 | Caspar South Water District | independent district | PO Box 744, Mendocino, CA 95460 | y |  |  | 66 |  | Familiar; not a participant | [21 empty] | Caspar, CA | Mendocino | North Coast, Region 1 | 46037 | n | 185
y |  | 1 | CAZADERO WATER COMPANY, INC. | Other | P.O. Box 423 6500 Cazadero Highway CAZADERO, CA 95421 | y | y | y | 157 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 0 | 0 | 2 | 1 | 2 | 2 | 2 | 0 | 0 | 1 | 0 | 2 |  | Cazadero, CA | Sonoma | North Coast, Region 1 | 49886 | n | 250 | GU | 1 Spring, wells (4) |  | 4 | 0-50 | $0 - $50 |  | 1. As of October 2016, the Division hadn't received results for a routine bacteriological sample collected from the distribution system of the WC during August 2016. 2. System is in violation of permit by operating Buckeye and Hotel Wells year round; they are considered to be groundwater under the direct influence of surface water during rainy winter months and their use is restricted to between May 15 and September 15 in the system's water supply permit. Additionally, the system doesn't monitor raw water for bacteria monthly. 3. The Division hasn't received results for a routine bacteriological sample collected in 10/14. | Poor condition | Water board staff thinks the water is corrosive but that is questionable. | B | 1. Total coliform monitoring and reporting violation for August 2016 2. Compliance Order No. 02_18_17R_011 3. Total coliform monitoring and reporting violation for 10/14 | 1. 10/21/16 2. 7/7/17 3. 12/18/14 |  |  |  | septic
|  | 1 | CHINOOK RV Resort WATER SYSTEM | Other | Del Norte | [28 empty] | Del Norte |  | 27200 | n
|  | 1 | Church Tree CSD | CSD | 251 Church Tree Road, Crescent City, CA 95531 | n |  |  | 26 | Flat rate + variable usage charge | [22 empty] | east of Crescent City along Elk Valley Road and adjacent to the Jedidiah Smith Redwood State Park | Del Norte | North Coast, Region 1 | 26544 | n | 40 | SW | purchases from City of Crescent City |  |  | 37.49 | $0 - $50 | Water from the Smith River is naturally filtered through the sand and gravel bed of the river and collected by intake lines 30 feet below the river. From there, water is pumped southward to the treatment facility off Kings Valley Road, where chlorine is added to meet State compliance standards. The City ceased adding fluoride on November 8, 2012 per ballot measure A | The Church Tree CSD receives water from the City of Crescent City. Crescent City obtains its water supply from the Smith River groundwater basin, which is located 8.5 miles north of the City. The basin produces approximately 2.9 million acre-feet of high quality water per year.Water is pumped out of the Smith River groundwater basin via a Ranney well, which has a capacity of 6,700 acre-feet per year. The District currently utilizes the following infrastructure: •One pump, •One 35,000 gallon water tank, •Approximately 10,00 lineal feet of water line, and •Two fire hydrants. The CTCSD’s water system is capable of serving 40 connections and is therefore operating at 65% of its total service capacity. The District water tank is currently not fenced and should be secured to comply with California code. The district should also plan on replacing the tank with hydrostatic pumps to maintain pressure and eliminate tank maintenance. (LAFCO 2018) | Fair condition/ Upgrades planned/ identified
y |  | 1 | CITY OF ARCATA | City | City of Arcata 736 F Street ARCATA, CA 95521 | y | y | y | 6134 | Increasing block (graduated) rate schedule | Familiar; lack resources to participate | Funded | 0 |  | 2 |  | 3 | 2 | 0 | 0 | 0 | 2 | 0 |  | 1 | 2 |  | 1 |  | 2 | 3 |  | Arcata Bayside | Humboldt | North Coast, Region 1 | 28277 | n | 19077 | GW | Purchases from HBMWD and Well (1) |  | 1 | 51-100 | $51 - $100 | All water introduced into the City's distribution system undergoes chlorination and fluoridation treatment. During the summer, this naturally filtered water is disinfected with chlorine. During the winter, it is further treated at a Turbidity Reduction Facility which reduces the occasional turbidity (cloudiness) in the source water. While turbidity itself is not a health concern, the State Water Resources Control Board (State Board) Division of Drinking Water (DDW) is concerned that at elevated levels, turbidity could potentially interfere with the disinfection process. | McKinleyville and the City of Arcata’s water supply are vulnerable to natural disaster, therefore, an emergency intertie was constructed to allow for the flow of water to occur between both systems if necessary. This line remains stagnant when not in use, therefore, a 5/8-inch bypass was installed which allows the water within the intertie to turnover and maintain its chlorine residual. All water that passes through the bypass is metered and currently enters into the City of Arcata’s water system from the McKinleyville system.” (McKinleyville CSD UWMP, 2015: P 13) | Adequate | Iron bacteria cause aesthetic water quality issues when our groundwater well is in operation. System performs frequent flushing to alleviate color & staining issues. |  |  |  | C | 1. NOV & transmittal of the 3/13 Compliance Evaluation Inspection Report. Deficiencies include: laboratory deficiencies; missing monitoring results, not recording effluent flow continuously, flow meters haven't been calibrated recently and calibration records couldn't be located. | 1.4/24/13 | sewer | The Glendale area receives wastewater service from the Fieldbrook-Glendale CSD. Glendale’s wastewater system is in very good condition overall and has approximately 166 connections. Flows currently range between 37,000 gpd during dry weather and 75,000 gpd during wet weather. The District has a contract to pump raw wastewater to the City of Arcata for treatment and disposal. The existing contract allows for up to 71,200 gpd average dry weather flow, indicating that the system has the capacity for approximately 80 to 100 more connections. Alternative solutions to treatment and disposal must be found to accommodate any development in excess of this. The City of Arcata has indicated it is not interested at this time in increasing the District’s contract amount and has recommended the District consider other alternatives. The District has approached the City of Blue Lake and will participate in other related studies to evaluate alternatives and costs for potential interconnection. | Good condition | The City of Arcata’s Best Management Practices for Stormwater Management considers runoff performance standards that result in site planning and design techniques to reduce storm flows, capture runoff water, and allow percolation or filtering before being discharged to channels, streams, or lakes. A significant portion of the manual information on Best Management Practices (BMPs) activities has been obtained from the California Stormwater Quality Task Force’s Best Management Practice Handbook and modified to suit the needs of the City of Arcata.
|  | 1 | CITY OF COTATI | City | 201 West Sierra Avenue COTATI, CA 94931 |  |  |  | 2562 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Sonoma | North Coast, Region 1 | 50667 | n | 7535 | GW | Purchased - SCWA - treated CC, wells (3) |  | 3 |  |  | The only required treatment is for bacterial and pathogen disinfection and pH adjustment. To accomplish this, the SCWA treats the water with chlorine for disinfection, and sodium hydroxide to adjust the pH before it is delivered to the various water dis-tricts and cities, including Cotati. | The City owns and operates a water supply and distribution system that supplies potable water to residences and businesses within the City limits. The City’s potable water supply comes primarily from water purchased from the Sonoma County Water Agency (SCWA) and water pumped from groundwater wells owned and operated by the City. The City’s main water supply is comprised of ground water from the Russian River permitted under a surface water diversion right for infiltration and groundwater from SCWA wells. In addition to the SCWA water supply, the City uses local groundwater supply from three municipal well sites located within city limits. Prior to 1992, the City used groundwater to supply more than half of its demands. More recently, the City’s water strategy has been to meet its demands by use of its SCWA water supply and to use its local groundwater supplies to supplement its needs during peak periods and during periods of drought. The City’s local groundwater supply is a key element of its drought contingency plan and is planned to remain as such throughout the 25-30 year planning horizon of the UWMP.4 The City actively seeks to balance the use of its SCWA water supplies and its local groundwater supplies in a way that ensures a sustainable yield of local groundwater. Additionally, as described in the UWMP, the City desires to implement a system that would allow for the delivery and use of recycled wastewater that is treated at the Santa Rosa Subregional System. There are currently three groundwater wells located within the City’s water distribution system. The City owns two water storage tanks. The West Sierra Avenue storage tank was constructed in 1997 and is a knuckle-roofed, welded steel storage tank with a total storage capacity of 1.0 million gallons. The facility is located west of Highway 101, just south of West Sierra Avenue, outside of the City limits. The tank has a base elevation over 249 feet and an overflow elevation of 274 feet. The high operating water surface elevation in the tank is 272 feet and the tank has a combined inlet/outlet pipe. The Cypress Avenue storage tank is a 100,000 gallon storage tank located at the end of Loma Linda Avenue. This storage tank is currently out of service; however the City plans to construct a new 400,000 gallon tank at this location in the future. | Fair condition/ Upgrades planned/ identified | [8 empty] | The City owns and operates a sanitary sewer collection system that provides sanitary sewer, or wastewater, service to approximately 1,200 acres in and around the City’s limits. The sanitary sewer system is comprised of four lift stations, approximately 140,300 lineal feet of collection piping ranging in size from six inches to 24 inches, approximately 484 manholes, approximately 150 cleanouts, and a 24-inch transfer interceptor which carries wastewater to the Santa Rosa Subregional Treatment Plant (also referred to as the Laguna Wastewater Treatment Plant) for treatment. The City’s Master Plan found that the current lift stations are capable of adequately conveying the existing and future (year 2035) design flow with the exception of the Quail Hollow Lift Station. However, the existing and future modeled capacity deficiency for this lift station was very minor. | Adequate
|  | 1 | CITY OF ETNA | City | P.O. Box 460 ETNA, CA 96027 |  |  |  | 383 | [24 empty] | Siskiyou | North Coast, Region 1 | 30089 | n | 769 | SW | Instream
|  | 1 | City of Ferndale | City | Ferndale, CA | y |  |  |  |  | Familiar; infrequent participation | Funded | [21 empty] | Humboldt |  | 38750 | n | [18 empty] | Wastewater flows from the municipal collection system by gravity to the headworks. Within the headworks, a comminutor and bar screen provide primary treatment. Wastewater from the headworks of up to 0.95 MGD is then pumped to a selector tank flowing by gravity to one of two rectangular extended aeration basins for biological treatment. From the aeration basins, wastewater flows by gravity to the adjacent rectangular clarifiers. Return activated sludge (RAS) is injected into the selector tank and aeration basins as appropriate to achieve maximum nitrogen removal efficiencies. Aerobically digested sludge is then pumped to a belt press for dewatering. The dewatered sludge is transported to the Humboldt County solid waste transfer station for disposal to a landfill. Clarified wastewater undergoes disc filtration prior to ultraviolet disinfection. From October 1 through May 14, treated wastewater is discharged to Francis Creek at its confluence with the Salt River. From May 15 through September 30, treated wastewater for irrigation use is applied to neighboring agricultural land. Ferndale has been recycling its water since the new WWTF was completed in 2012. Facility improvement projects include: need for improved I&I, address issues with the equalizing storage pond, the UV disinfection system, and a composting facility. | Good condition | The City of Ferndale’s stormwater drainage system consists of a series of drainage inlets and underground pipes that eventually drain into the Salt River. Annual rainfall averages between40-60 inches. As mentioned previously, the hydraulic conditions of the Francis Creek / Salt River watershed have resulted in a higher sediment load and reduced flows that contribute to flooding during periods of peak stormwater runoff. This is further impacted by undersized drainage facilities and challenges re taining/detaining water onsite due to a high water table and relatively flat land. he city is currently in the early stages of updating its Drainage Master Plan to include watershed mapping, hydraulic modeling, and up-to -date stormwater infrastructure inventory to assess the current system condition and to identify drainage system improvements. This will incorporate watershed-wide restoration planning that is ongoing for Francis Creek and the Salt River.
|  | 1 | City of Fortuna WWTP | City | [29 empty] | Humboldt |  | 49403 | n | [15 empty] | Admin civil liability | 5.23.2018
y |  | 1 | CITY OF FORTUNA | City | City of Fortuna P.O. Box 5 FORTUNA, CA 95540 | y | y | y | 4377 | Monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 3 |  | Fortuna, CA | Humboldt | North Coast, Region 1 | 49403 | n | 11649 | GW | Wells (5) |  | 5 | 100-150 | $101 - $150 | The City’s water supply comes entirely from five groundwater wells (four active and one emergency stand-by) located at the City’s corrosion control facility. The combined rated capacity of all wells is 4,000 gpm, or 5.76 MGD. Water is chlorinated in the wells as a precautionary measure due to the annular seals being less then 50 feet deep and then pumped from the wells into a 120,000 gallon wet well, containing three 100 horsepower booster pumps that pump water into the City’s distribution system. | The City’s water supply comes entirely from five groundwater wells (four active and one emergency stand-by). The well site includes disinfection and corrosion control facilities. It is believed that this water source is tied to the Eel River. The combined rated capacity of all wells is 4,000 gpm, or 5.76 MGD. Water is chlorinated in the wells as a precautionary measure due to the annular seals being less than 50 feet deep and then pumped from the wells into a 120,000 gallon wet well, containing three 100 horsepower booster pumps that pump water into the City’s distribution system. The distribution system is divided up into eight pressure zones and contains a series of pumps, water tanks, reservoirs, and hydropneumatic tanks. The combined storage capacity of the system is approximately 7.3 million gallons. Some pressure zones do not have adequate storage, but can be provided water through booster stations with portable generators on site. The city’s distribution system includes 37 miles of water piping. The system is composed of both new and old piping, with a mix of older asbestos-cement and cast-iron pipe, and newer polyvinyl chloride or PVC pipe. Water system infrastructure deficiencies have been addressed in the city’s five Year CIP. | Fair condition/ Upgrades planned/ identified |  |  |  |  | C | 1. NOV & transmittal of the 3/13 Compliance Evaluation Inspection Report. Deficiencies include: biosolids wasting rates insufficient to maintain system equilibrium; reporting erros including not reporting completed analyses and listing incorrect date for analyses. | 1. 4/24/13 | sewer | The City of Fortuna’s wastewater system is in good condition overall, and was expanded in 2006 to improve capacity and performance. The City’s wastewater facilities are permitted to treat up to 1.5 MGD mean daily dry weather flow averaged over a period of one calendar month. Existing dry weather flows are currently 0.95 MGD. Therefore, the treatment facility is operating at approximately 63% of its dry weather flow capacity. However, wet weather flows continue to pose a problem for the City. The most significant collection system issues relate to existing collection system pipingcapacities. The 12- and 15-inch sewer lines located between 9th and 12th Street, Loni Drive, and the area between I Street and L Street, respectively have flat grades and are subject to I/I. The old gravity lines located along Newburg Road are considered at capacity and not suitable for handling new or increased flows. There is also a lack of collection system piping in currently undeveloped areas. Wastewater system deficiencies are being addressed in the city’s Five-Year Capital Improvement Program. The 2007 – 2008 CIP lists eighteen wastewater projects to be completed over the next five years. | Fair condition/ Upgrades planned/ identified
y |  | 1 | CITY OF ROHNERT PARK | City | 600 Enterprise Drive ROHNERT PARK, CA 94928 | y | n | y | 9572 | Increasing block (graduated) rate schedule | Familiar; regular participant | Unfunded | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 2 |  | Rohnert Park, CA | Sonoma | North Coast, Region 1 | 71576 | n | 42067 | GW | primarily purchases treated water from Wohler Caissons; wells (20) |  | 20 | 100-150 | $101 - $150 | Both the City of Rohnert Park and the Sonoma County Water Agency chlorinate the water that we provide to our customers. Due to seasonal variations in water source and the demand for water, you may notice minor fluctuations in the chlorine taste of our water. | [6 empty] | D | 1. Notice of Violation of SWRCB General Permit for Storm Water Discharges Associated with Construction and Land Disturbance Activities and Confirmation of Corrective Actions | 1. 3/7/16 | sewer
y |  | 1 | CITY OF SANTA ROSA | City | 69 STONY CIRCLE SANTA ROSA, CA 95401 | y | y | y | 52474 | Increasing block (graduated) rate schedule; For residential, there is a sewer base (amount of water in winter), Tier 2 is over and above that. For irrigation, Tier 1 is amount of water needed for landscape considering area and evapotranspiration, 125% of that rate is 2nd tier Flat rate for industry. Water and sewer combined, see above for how it's split, Colin can provide greater detail on all of this. Might be over $150, definitely not less than $100. Subsidized program for low - income residents using revenue from non-water sales and other income to reduce fixed rate charge and then do water efficiency work to reduce amount of water needed. | Familiar; regular participant | Funded | 0 | 1 | 2 | 0 | 2 | 2 | 1 | 0 | 0 | 1 | n/a | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | Santa Rosa, CA | Sonoma | North Coast, Region 1 | 46037 | n | 178488 | GW | purchase treated from Wohler Cassion, spring (1), wells (4) |  | 4 | 100-150 | $101 - $150 | Water collected from the Russian River through deep collector wells requires no additional treatment with the exception of chlorine which is added for disinfection, and sodium hydroxide which is added to adjust the pH of the water to reduce corrosion of lead and copper plumbing fixtures. |  |  | With water supply wells, there is a taste and odor issue with sulfur and manganese - about 5 - 10% of water use - during April -October when there's high demand. Water from SCWA - no issues primary or secondary. well issues only secondary. | [6 empty] | sewer
|  | 1 | CLEAR CREEK WATER COMPANY | other | [6 empty] | Familiar; infrequent participation | Unfunded | [21 empty] | Sonoma | North Coast, Region 1 | 63229 | n
y |  | 1 | CLOVERDALE, CITY OF | City | 124 North Cloverdale Boulevard CLOVERDALE, CA 95425 | y | y | y | 3253 | Monthly/ annual flat rate; Flat rate with "per unit" water usage charge and water conservation rate increases determined by water conservation stage. | Familiar; regular participant |  | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 2 |  | Cloverdale, CA | Sonoma | North Coast, Region 1 | 63229 | n | 9157 | GU | Wells (7), four of which are under the influence of surface water |  | 7 | 100-150 | $101 - $150 | [10 empty] | sewer
| y | 1 | COLONIAL PARK | other |  | n |  |  | 100-250 | monthly/ annual flat rate | [7 empty] | 1 | [13 empty] | 1 | Santa Rosa, CA | Sonoma | North Coast, Region 1 | 57639 | n | 250-500 |  |  |  |  | 0-50 | $0 - $50
|  | 1 | COPCO LAKE MWC | Mutual | 16238 VALERIE RD. MONTAGUE, CA 96064 |  |  |  | 65 | [24 empty] | Siskiyou | North Coast, Region 1 | 40938 | n | 181 | GW | SP - spring, raw, and well
|  | 1 | COVE MOBILE VILLA | other | 6431 Old Hwy 99 S, Yreka, CA 96097 |  |  |  | 70 | [24 empty] | Siskiyou | North Coast, Region 1 | 25493 | n | 128 | GW | Well |  | 1
y | y | 1 | COVELO C.S.D. | CSD | 76270 Grange Street (P.O. Box 65) COVELO, CA 95428 | y | y | y | 265 | Monthly/ annual flat rate | Familiar; infrequent participation | Funded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Covelo, CA | Mendocino | North Coast, Region 1 | 29167 | p | 1255 |  |  | ~ 481 (# of households) |  | 51-100 | $51 - $100 | [10 empty] | sewer | The CCSD sewer system consistsof four major collection basins; threeof them north of Town Creek, and the other south of the creek. The smallest of the three northern basins lies along East lane within the northeast corner of the CCSD. Wastewater in this basin flows by gravity to a lift station near the northern limit of the Commercial Street sewer main. The lift station pump ... lifts collected wastewater to the terminal manhole on the Commercial Street main where it joins wastewater generated in the largest northern collection basin situated within and west of Commercial Street.The largest collection basin located north of Town Creek and primarily west of Commercial Street includes contributors from parcels near the intersection of Howard Street and Crawford Road at the extreme northwest side, and from the contributors within the more urban area bounded by Howard Street on the north and Commercial Street on the east. All wastewater from these two northern collection basins flows by gravity toward Town Creek, and passes under the creek through an inverted siphon. A main interceptor sewer line located just south of Town Creek conveys collected wastewater east to the wastewater treatment plant. The overall collection system serves a geographic area of about 185 acres, including approximately 35 acres that lie outside of the existing district boundary. The collection system service area contains approximately 200 residential users, 51 commercial users, 9 institutional users, 2 public uses, and 2 other uses that do not fit a standard user category. The sewer main piping comprising the collection system in the largest of the three northern basins includes approximately 3,900 linear feet of 8-inch diameter and 14,575 linear feet of 6-inch diameter asbestos-cement pipe (transite pipe). There are approximately 45 manholes and 10 mainline cleanouts in this portion of the overall system. Originally, the collection system flowed towards Commercial Street, and flowed south to a point 1500 feet south of Elberle Street where it turned eastcrossing under Town Creek a second time to the treatment plant. In 2007, the Town Creek Bridge was bypassed with 654 feet of twelve inch line that directs sewage from north of Town Creek straight to the plant. The old line passing under the bridge was plugged.From the new manhole just north of the bridge to the manhole at Commercial and Howard Streets, 2,064 feet of sewer line were replaced with 10 inch SDR-26 PVC pipe. All 2,657 feet of sewer line on Howard Street was replaced with 8 inch SDR-26 PVC. Sewer line replacement included new manholes. In its 2006 report, SHN Engineers listed a number of plant deficiencies:Grit, rocks, rags and other damaging materials were not effectively removed from the effluent flow. Equipment is damaged and ponds fill up with these materials requiring significant dredging.Headworks and pretreatment processes were significantly problematic. The headworks structure was much too small to allow proper maintenance of equipment. The comminutor was outdated, doesn’t work, and needed replacement. New equipment to remove more of the damaging materials entering the system was needed.The septage receiving system at that time relied on self-monitoring of septage haulers regarding quantity, pH, etc. SHN recommended an automated septage receiving system be installed.The two oxidation ponds suffer from varying degrees of seepage through their walls caused by rodents, roots, etc. At the time of the report groundwater tests were still being conducted to determine if the seepage through the pond bottoms was significantly affecting groundwater quality.Both holding ponds typically dry out during hot summer months, when practically all the treated effluent is evaporated from the oxidation ponds. This has caused the bentonite linings to crack and leak. When the ponds receive treated effluent it leaks uncontrollably into the groundwater. Attempts to keep the bottoms of the ponds moist during the hot months have not been effective because of an inadequate supply of well water and the inability to apply the water evenly across the surface.In recent years evaporation and seepage from the oxidation and holding ponds has all but eliminated the need to discharge treated effluent into Grist Creek. As a result the final filtering and disinfection systems have not been used in many years. This has led to significant problems with the pumping,filtering and disinfection systems. A number of significant public health threats are caused by the District’s sewer system. Elementary School -raw sewage has overflowed out of the system in front of the school for 30 years.Overflow in Other Locations -At least two other locations had occasional overflows out of the system into streets.Back up into Homes -homes in two areas of the District occasionally had sewage backing up flowing into their yards.These problems mostly happen during storms.SHN states that both capital improvements to the system and upgraded maintenance practices are needed to correct these problem. The majority of effluent disposal occurs through percolation into the groundwater beneath the holding ponds, which is in violation of the District’s existing NPDES permit5.The uncontrolled percolation that is occurring at present does not adequately protect the quality of groundwater underlying the plant area. CSD has been busy in recent years correcting numerous problems with their collection system. The remaining system problems noted above create significant constraints on the ability of staff to properly maintain the system. The “solutions” to the indicated problems are mostly investment in upgraded facilities; the difficulty is in obtaining sufficient funds for the “solutions”. | Poor condition
|  | 1 | COVELO MOBILE HOME PARK | other |  |  |  |  | 19 | [24 empty] | Mendocino | North Coast, Region 1 | 29167 | n | 30 | GW | Wells (2) |  | 2
y |  | 1 | COVINGTON MILL MWC-DIVISION B | Mutual | P.O. BOX 144 TRINITY CENTER, CA 96091 | n | y | dk | 99 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 0 | 1 | 1 | 0 | n/a | n/a | 0 | 0 | 0 | 1 | 0 | 0 |  | 1 | 0 | 0 | 1 | 3 | 2 | 1 | CMMWC, B. Hwy and Lake Forest Drive | Trinity | North Coast, Region 1 | 32321 | n | 99 | GW | Wells (7) |  | 7 | 0-50 | $0 - $50
|  | 1 | Creekside Cabins & RV Resort | other | PO Box 279, Lakeport, CA 95453 |  |  |  | 55 | [24 empty] | Mendocino | North Coast, Region 1 | 45299 | n | 124 | GW | Well |  | 1 | [6 empty] | 0 | 1. Bacteriological monitoring violation | 2015-12-15
y | y | 1 | CRESCENT CITY, CITY OF | City | 377 J STREET CRESCENT CITY, CA 95531 | y | y | y | 3416 | uniform rate schedule | Familiar; regular participant | Funded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 |  | Crescent City, CA | Del Norte | North Coast, Region 1 | 26544 | n | 15600 | GW | Well |  | 1 | 51-100 | $51 - $100 | Using natural filtration through the sand and gravel bed 30 feet below the river, water is collected from intake lines (or fingers) driven into the gravel bed. Water is pumped southward to the treatment facility off Kings Valley Road, where chlorine is added to meet State standards. This is the extent of treatment. The City of Crescent City ceased adding fluoride to its water supply on November 8, 2012 per ballot Measure A. Water from the Smith River is naturally filtered through the sand and gravel bed of the river and collected by intake lines 30 feet below the river. From there, water is pumped southward to the treatment facility off Kings Valley Road, where chlorine is added to meet State compliance standards. The City ceased adding fluoride to its water supply on November 8, 2012 per ballot measure A. Under Water Resources Control Board water rights permits, the appropriation from the Smith River (underflow) is specified as an average of 12.8 cubic feet per second (cfs) (8.3 million gallons per day) with a maximum annual diversion of 3,666 AFY (1,194 million gallons per year) (Freshwater Environmental Services, 2014. | Crescent City Adopted MSR/SOI 10 2019 The CCHA is developing an affordable housing project with Project Based Vouchers (PBVs) as a partial funding source. They have secured property, committed vouchers and selected a contractor, Danco Communities, and entered into a deferred development agreement to build the “Harbor Point Apartments” an affordable housing project with subsidized units. Water Services. The Crescent City water system provides water collection, treatment and distribution to the incorporated city of Crescent City, certain unincorporated areas near the city, and the Pelican Bay State Prison through a system comprised of one well in the Smith River, and 60 miles of water mains. Under contractual agreements, the City also delivers water within the Bertsch-Oceanview Community Services District (BOV CSD), the Church Tree Community Services District (CT CSD), Crescent Fire Protection District W-1 (FDW1) and the Meadow Brook (MB) area of the Del Norte Flood Control District. The Smith River provides an abundant supply of high quality fresh water. | Adequate |  |  |  |  | C | 1. Administrative Civil Liability Complaint: Discharger's self-monitoring reports for the complaint period document seven violations of effluent limitations. All seven violations are subject to MMPs. 2. Order No. R1-2017-0002, Waste Discharge Requirements and Water Recycling Requirements for the City of Crescent City Wasteater Treatment Facility, Del Norte County | 1. 7/22/2016 | sewer | Major renovations and upgrades to the Crescent City wastewater treatment facility were completed in 2010. The Wastewater Treatment Facility (WWTF) consists of new influent pumping equipment and controls, new grit removal system, primary clarifier modifications, upsized and upgraded site piping, removal of underground storage tank and contaminated soil, and addition of membrane bioreactors, ultraviolet disinfection and effluent pumping for the production water that comports with the California Code of Regulations Title 22 (Title 22)requirements.The City's WWTF is capable of producing, tertiary-treated recycled water meeting Title 22 Water Recycling Criteria and the City looks for recycled water use opportunities. The reclamation system capacity is 0.6 mgd; however, the membrane bioreactor can treat up to 1.6 mgd. Effluent that is not recycled is discharged to the Pacific Ocean. The 24- inch diameter ductile iron pipe outfall discharges into a rocky slot in the surf zone adjacent to Battery Point Lighthouse and has an effluent conveyance capacity up to 13 mgd (UWMP). | Good condition
|  | 1 | CRIVELLI'S WATER SYSTEM | Other | Del Norte | [28 empty] | Del Norte |  | 27200 | n
| y | 1 | DEL NORTE COUNTY COMMUNITY SERVICE AREA | County Dist | 981 H STREET, SUITE 101, CRESCENT CITY, CA 95531 | y | y |  | 2000 | monthly/ annual flat rate | Familiar; regular participant | Funded | [5 empty] | 1 | [10 empty] | 1 |  |  |  | Unincorporated areas of Del Norte County. | Del Norte |  | 26544 | n | 6000 |  |  |  |  | $6.50/ month | $0 - $50
|  | 1 | DELORES LANE WATER SYSTEM | other | 1746 Olivet Road SANTA ROSA, CA 95401 |  |  |  | 17 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 50 | GW | Wells (2) |  | 2
|  | 1 | Dolphin Isle Marina | other | 32399 Basin St. FORT BRAGG,CA 95437 |  |  |  | 85 | [24 empty] | Mendocino | North Coast, Region 1 | 31027 | n | 560 | GW | Well |  | 1
y | y | 1 | DORRIS, CITY OF | City | P. O. BOX 768 (307 S. Main Street) DORRIS, CA 96023 | y | y | y | 481 | monthly/ annual flat rate | Familiar; lack resources to participate | Unfunded | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | N/A | 3 | 2 | 2 | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 2 | Dorris, CA | Siskiyou | North Coast, Region 1 | 31923 | n | 887 | GW | Wells (2) |  | 2 | Majority of services Resid water-41.75 month/Resid sewer-18.25 Comm1 water-29.04 Sewer 11.62. We have a few like school, clinic and mill that are a higher rate 51-100 | $51 - $100 |  |  |  | City has to treat for smell problem; Strong sulfur odor |  | 1. Citation for violation of the coliform MCL January 2013 | 1. 3/29/2013 |  |  |  | sewer
|  | 1 | Dos Rios Mutual Water Company | Mutual | 11801 Dos Rios Road, Dos Rios, CA 95429 | n |  |  | 24 | [23 empty] | Dos Rios, CA | Mendocino | North Coast, Region 1 | 23315 | n | 21 | GW | Well (1) Inactive |  | 0 | $41 - $80 per month | $51 - $100 |  | The Company owns and maintains one well and approximately four to five miles of pipeline. | Adequate
|  | 1 | DOWNTOWN GRATON MUTUAL WATER SYSTEM | Mutual | [29 empty] | Sonoma |  | 99141 | n
|  | 1 | EAST AUSTIN CREEK MUTUAL WATER COMPANY | Mutual | PO Box 463 CAZADERO,CA 95421 |  |  |  | 16 | [23 empty] | Cazadero, CA | Sonoma | North Coast, Region 1 | 49886 | n | 15 | GW | Well (1) |  | 1
|  | 1 | EL CRYSTAL MOBILE HOME PARK | Other | 3280 Santa Rosa Ave, Santa Rosa, CA 95407 |  |  |  | 58 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 130 | GW | Wells (2) |  | 2 | [6 empty] | A | 1. Compliance Order 02_18_17R_009 | 1. 6/23/17
|  | 1 | EL PORTAL MOBILE ESTATES | Other | 871 38TH AVENUE SANTA CRUZ, CA 95062 |  |  |  | 122 | [24 empty] | Sonoma | North Coast, Region 1 | 29250 | n | 200 | GW | Wells (2) |  | 2 | [6 empty] | C | 1. TCE MCL Violation for third and fourth quarter 2014 | 1. 2/19/17
|  | 1 | ELK COUNTY WATER DISTRICT | Water Dist | PO Box 195, Elk, CA 95432 Alternative Address: 6129 S Highway 1 Elk, CA 95432 | y |  |  | 101 | increasing block | [22 empty] | Elk, CA | Mendocino | North Coast, Region 1 | 39667 | n | 380 | GU | Wells (2) |  | 2 |  |  |  | ECWD’s water system is classified as a ‘community water system’ and includes a water treatment plant (WTP), one well, and several miles of pipeline. The District does not own any major equipment. The District owns the following infrastructure:  water treatment plant;  two water storage facilities – 30,000 and 84,000 gallons  pipes;  One new supply well;  parcel of land where the well is located (one parcel is owned and ECWD has an easement over the second parcel); and  parcel of land that houses a storage shed, community center, and volunteer fire station. Projects or impacts to Greenwood Creek have the potential to negatively affect the District’s water supply. For example, a project to replace the Greenwood Creek Bridge resulted in temporary impacts to the District. | Adequate | [8 empty] | The WTP uses direct filtration to remove 99 percent of Giardia lamblia cysts and 90 percent of viruses. | Adequate
|  | 1 | EMERALD FOREST | Recreation Area | Humboldt |  |  |  | 1 | [23 empty] | Transient, recreationalists | Humboldt | North Coast, Region 1 | 50417 | n | 200 | GU | Wells (2) |  | 2 |  |  |  | T2 treatment plant
| y | 1 | END-O-VALLEY MUTUAL WATER COMPANY | Mutual |  | n | n |  | 25-50 | monthly/ annual flat rate | Unfamiliar; disinterested | [14 empty] | 1 |  |  | 1 |  |  | 1 |  | Sonoma | North Coast, Region 1 | 46037 | n | 100-250 |  |  |  |  | $50-100 | $51 - $100
|  | 1 | EUREKA, CITY OF, ELK RIVER WWTP | other | [29 empty] | Humboldt |  | 20346 | n | [15 empty] | Admin Civil Liability | 2018-06-07
y | y | 1 | EUREKA, CITY OF | City | 3575 W Street, EUREKA, CA 95501 | y | y | y | 9944 | Uniform rate schedule with volume charges | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 0 | 0 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 2 |  | Eureka, CA | Humboldt | North Coast, Region 1 | 20346 | n | 32815 | GWP | purchase treated from HBMWD |  |  |  |  | The City’s water treatment plant provides chlorination and fluoridation treatment. | The City of Eureka purchases water from a wholesaler, Humboldt Bay Municipal Water District. Under the agreement between the District and The City of Eureka, the deliveries from the District to the City are considered to be deliveries of the City's water, emanating from its own water rights not those of the District. Deliveries to the City in excess of the City's water rights are considered deliveries of the District's water. Water is supplied to two primary pressure zones: the Low Zone and the High Zone. A 24-inch steel main supplies the low zone by gravity, and a 16-inch steel force main supplies the high zone with pumping. The high zone pumping capacity is 2,400 gallons per minute (GPM). The low zone is fed by gravity from the 20-MG reservoir, with an increased capacity flow of up to 6,000 GPM when using two 50-HP vertical turbine pumps and one backup 100-HP pump. The system’s total storage capacity is 22.3 MG, comprised of a 20-MG raw water storage reservoir, a 1-MG ground-level steel tank, a 500,000-gallon ground-level steel tank, a 500,000-gallon elevated steel tank, and a 300,000-gallon clear well. The City’s distribution system has normal deficiencies for a system of its age, which includes an aging piping system and low-pressure and fire-flow issues. Planned water distribution system improvements within the City include the following: Repairs and replacement of deteriorated, undersized, and aged mains, valves, and services in accordance with the Water Distribution System Annual Replacement and Maintenance Program Planned water treatment system improvements Corrosion control and upkeep of water storage tanks A new pump station at the Harris and K Streets tank farm Replacement of fire hydrants that do not meet the City’s current standards for fire flow capacity Installation of water meters at all City facilities | Fair condition/ Upgrades planned/ identified | [7 empty] | sewer | The City’s wastewater collection system contains approximately 125 miles of sewer main, 9,500 service laterals, 18 lift stations, 4 major pump stations, and associated force mains. The system collects and conveys between 1.6 and 1.8 billion gallons of wastewater per year. The City also collects wastewater from HCSD, which serves the unincorporated areas east and southeast of the city limits. The City operates the Elk River Wastewater Treatment Plant (WWTP) located in the southwest portion of the City near the mouth of the Elk River; the WWTP was designed in 1981 for the purpose of treating, storing, and disposing of wastewater. The WWTP serves customers within the City of Eureka and also treats wastewater from the surrounding unincorporated areas served by HCSD. The total City, County, and HCSD population served by the WWTP is approximately 45,000. The City’s wastewater collection system is experiencing deficiencies that are typical of a collection system of its age, including Inflow and Infiltration (I/I), pipe condition deterioration (with a majority being clay pipe), aging pumping systems, and some capacity limitations. Capacity concerns occur at a few locations in the collection system during significant rain events. The City has planned the following WWTP and collection system upgrades: Wastewater Collection System Replacement and Maintenance Program Implementation Wastewater Inflow and Infiltration Reduction Program - A multi-phased, multi-year program for reducing I/I into the wastewater system by implementing capital improvement projects in accordance with program recommendations based on field tests. Sewer Lift Station and Pump Station Upgrades including a change to VFD pump control Extended Fuel Storage Facility Cross-town Interceptor Maintenance Installation, Replacement, Repair, or Relocation of Storm Drainage Facilities City-wide. | Fair condition/ Upgrades planned/ identified | Much of the City’s existing storm drainage network is old and undersized, depending upon inadequate gutter flow and undersized pipes and drop inletsxvii. There is street flooding during the rainy season. Some of the City’s sloughs and gulches, serving as natural drainage networks, have been filled, restricted, and/or altered. Most of the natural networks are unimproved, relatively deep, and have adequate capacity for a 100-year storm event. However, due to erosion and siltation, resulting in reduced capacity at some storm drain inlets and outlets, a few of the gulches experience flooding. No actual drainage easements exist for many of the City’s natural drainage networks; due to lack of access, maintenance and replacement within these gulches can be difficult. (LAFCO) The City of Eureka’s Storm Water Quality Management and Discharge Control Ordinance, contains detailed BMP requirements that are comprehensive, are consistent with the Federal Clean Water Act and the Porter-Cologne Water Quality Control Act , and are a very effective means of reducing stormwater pollution that are a result of development activities.
|  | 1 | FARMER WATER SYSTEM | other | [29 empty] | Sonoma |  | 99141 | n
|  | 1 | FERNDALE - DEL ORO WATER CO. | Public Utility | DRAWER 5172 CHICO, CA 95927 | y |  |  | 759 | increasing block | [23 empty] | Humboldt | North Coast, Region 1 | 38750 | n | 1998 | GW | Springs - raw (2), well |  | 1 | wastewater = 66.02/month | $51 - $100 |  | Ferndale water sources originate from groundwater and are known as the High Line Springs, Low Line Springs, and Van Ness Well. These sources have a combined maximum production capacity of approximately 518,000 gallons per day. As of 2012, existing maximum daily demands are estimated at 208,000 gallons per day, which is approximately 40% of source capacity. Approximately 70% of the water is pulled from the springs, with back up production from the Van Ness Well. | Adequate | [12 empty] | 1
y | y | 1 | FIELDBROOK GLENDALE C.S.D. | CSD | PO Box 2715, McKinleyville, CA 95519 P.O. BOX 95 EUREKA, CA 95502 | y | y | y | 584 | Monthly/ annual flat rate; Increasing block (graduated) rate schedule | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | Fieldbrook & Glendale | Humboldt | North Coast, Region 1 | 20346 | n | 1927 | GWP | CC Humboldt Bay MWD purchased |  |  | Water $45 Wastewater $76 | $101 - $150 | purchases treated water from HBMWD | The Fieldbrook-Glendale CSD’s receives treated water through the HBMWD and is not limited by either source or treatment capacity with respect to its ability to serve new connections. The only major deficiency associated with the existing system and the existing development they serve is lower than desirable water pressure within some localized areas. In addition, a stand by generator is needed at the main (Lyman Rd) booster pump station and a new roof is needed on the redwood tank. The Fieldbrook-Glendale CSD may need to expand its water distribution system at some point to serve this additional growth. The Fieldbrook-Glendale CSD purchases treated water from Humboldt Bay Municipal Water District (HBMWD) for delivery to its customers. The FGCSD system begins at a water meter just north of the intersection of Fieldbrook Road and includes over 10 miles of water mains, one booster pump station, and one 400,000 gallon water tank. Water quality is excellent and meets or exceeds State standards. Some localized pressure problems are experienced by some residences and this problem needs to be addressed before any additional growth is to occur. Other water system improvements anticipated to be needed include the installation of a standby (emergency) generator at the booster pump station and the construction of an additional reservoir. In the Glendale area, low water pressure is among the primary concerns voiced by local residents. Water service within the Glendale area is generally very good, with the exception of some low pressure areas. The only major deficiency associated with the existing system and the existing development they serve is lower system pressure within some localized areas. The Glendale area does not have any storage in its service area and normally relies on the HBMWD water reservoirs, although the Fieldbrook reservoir can be used to back feed to this area in an emergency. The Blue Lake FPD Fire Chief, who has fire protection responsibility for most of Glendale, states that additional water storage is required within Glendale for fire suppression as well as domestic water needs (Personal Communication, January, 2017). Glendale will need to expand its water system infrastructure to serve additional growth. The Fieldbrook-Glendale CSD receives treated water through the HBMWD and is not limited by either source or treatment capacity with respect to its ability to serve new connections. | Good condition | [7 empty] | sewer | The Glendale area receives wastewater service from the Fieldbrook-Glendale CSD. Glendale’s wastewater system is in very good condition overall and has approximately 166 connections. Flows currently range between 37,000 gpd during dry weather and 75,000 gpd during wet weather. The District has a contract to pump raw wastewater to the City of Arcata for treatment and disposal. The existing contract allows for up to 71,200 gpd average dry weather flow, indicating that the system has the capacity for approximately 80 to 100 more connections. Alternative solutions to treatment and disposal must be found to accommodate any development in excess of this. The City of Arcata has indicated it is not interested at this time in increasing the District’s contract amount and has recommended the District consider other alternatives. The District has approached the City of Blue Lake and will participate in other related studies to evaluate alternatives and costs for potential interconnection. | Good condition |  | 1 | 1
|  | 1 | FIRCREST MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma |  | 99141 | n
|  | 1 | Forestville Water District | Water Dist | [29 empty] | Sonoma | North Coast, Region 1 | 38792 | n | [12 empty] | Category 1 Pollutant (Effluenct Violation for Group 1 Pollutant) | 1/31/2019, 1/22/2019; 2/14/2019; 2/28/2019; 3/12/2019
| y | 1 | FORT BRAGG MUNICIPAL IMP DISTRCT | Municipal Imp Dist | 416 N. FRANKLIN ST., FORT BRAGG, CA 95437 | y | y |  | 2800 | Monthly/ Annual Flat Rate: Monthly flat rate that increases by unit. | Unfamiliar; interested | [6 empty] | 1 | [10 empty] | 1 |  |  | 1 | Fort Bragg, Mendocino County. | Mendocino | North Coast, Region 1 | 31027 | n | 7000 | [17 empty] | The public wastewatertreatment system includes collection, treatment, and discharge facilities. The wastewater system serving the City of Fort Bragg is owned by the Fort Bragg Municipal Improvement District (MID/District)No. 1 and isoperated and maintained by the Cityat the expense of the District. The District boundary is larger than the City boundary. The Fort Bragg MID No. 1(District)was formed to acquire and construct wastewater system improvements including a wastewater treatment plant and to provide for the incurring of indebtedness for the costs and expansion of such improvements. Any territory annexed to the MID is subject to all the liabilities, including previously authorized taxes, benefit assessments, fees or charges for services, and is entitled to all benefits of the District. (LAFCo, 2008)The Wastewater Treatment Plant (WWTP) is located at 101 West Cypress Street in Fort Bragg. The WWTP operates under Waste Discharge Requirements pursuant to Order No. R1‐2015‐0024, NPDES No. CA0023078, and WDID No. 1B84083OMENissued by the North Coast Regional Water Quality Control Board on June 4, 2009 (Fort Bragg, March 2017). The MID serves approximately 2,450 residentialwastewaterconnections,350commercial dischargers,and one industrial customerwithin the District,and serves MacKerricher State Park located outside the District(Fort Bragg, July 2017). The MID wastewater system is comprised of over 25 miles of gravity-fed pipelinesand pressure force mains, six sewage lift stations,theWWTP,and an ocean outfall pipeline that extends690 feet into the Pacific Ocean. Over the past five years, the North Coast Regional Water Quality Control Boardh as issued two settlement agreements for Administrative Civil Liability (ACL)to the District, both were satisfactorily addressed. The most recent ACL (R1-2016-0049) consists of two compliance projects to satisfy the minimum mandatory penalties. These exceedances include biochemical oxygen demand (BOD), total suspended solids (TSS), Total Coliform and Total Chlorine Residual. The compliance projects involve installation of an influent flow meter and installationofsodium hypochlorite and sodium bisulfite analyzers. The previous ACL (R1-2014-0035) included a compliance project to complete the designphaseof the WWTPUpgrade Projectin order to improve BOD and TSS effluent discharge. These compliance projects have been completed, with the exception of the influent flow meter which is scheduled for installation in September, and satisfactorily addressed the RWQCB concerns.(Fort Bragg, March 2017; Fort Bragg, July 2017) Currently, the WWTP wet weather treatment capacity is exceeded several times a year due to very high flows of stormwater and groundwater into the wastewater collection system caused by infiltration and inflow (I/I) and cross-connection between storm drains and sewer lines. I/I is problematic for multiple reasons but especially because of the potential for sanitary sewer overflows (SSOs) and penalties for exceeding effluent limitations when the WWTP cannot operate as designed. The aging infrastructureof the wastewater system and the peak flow volume during wet weather events are the primar yfactors influencing the District’s ability to provide wastewater services to customers. | Storage capacity insufficient
|  | 1 | Fort Bragg City WWTP | City | [29 empty] | Mendocino |  | 31027 | n | [15 empty] | Expited Payment Letter | 6.16.17
y | y | 1 | FORT BRAGG, CITY OF | City | 416 N. FRANKLIN STREET FORT BRAGG, CA 95437 | y | y | y | 2822 | Seasonal rate schedule | Familiar; infrequent participation | Unfunded | 0 | 2 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 2 |  | Fort Bragg, CA | Mendocino | North Coast, Region 1 | 31027 | n | 7250 | SW | IN - Newman Gulch Intake, Noyo River Pump Station, Simpson Creek Intake |  |  | 100-150 | $101 - $150 |  | The City’s water system is comprised of three surface water sourcesincluding the new Summers Lane Reservoir constructed in 2015; threeraw water transmission mains; two raw water storage ponds located at the WTP; the WTP that was originally constructed in the 1950’s and upgraded in the 1980’sand has a capacity of2.2 million gallons per day (MGD); two 1.5 million gallon (MG) steel storage tanks and one 300,000 gallon storage tank; over 30 miles of distribution lines that deliver water throughout Fort Bragg; and one booster pump station for the East Fort Bragg pressure zone (LAFCo,2008). Additionally the City has funding for and will add an additional1.5 million gallon finished water storage tank in Fiscal Year 2017-18. (LAFCo,2008; Fort Bragg, July 2017) The City’s water supply system draws raw water primarily from the Noyo River with the limitation that pumping does not exceed 3.0 cubic feet per second (cfs).The Noyo River direct diversion flows by gravity into a 5,000 gallon wet well and is then pumped via pipeline to the WTP from a pump station on the river bank.The Newman Reservoir is an on-stream reservoir located on a 54-acre parcel owned by the City of Fort Bragg and impounds water from the Newman Gulch. The Summers Lane Reservoir is a new reservoir with a capacity of 45 acre-feet (AF) located on this same property. The Summers LaneReservoir is an off-stream storage facility that holds water from Waterfall Gulch .Approximately 20% of the City’s water supply during the summer months is drawn from the Newman and Summers Lane Reservoirs and approximately 25% throughout the year is from the Waterfall Gulch diversion, all of which are gravity fed through a single ten-inch pipeline to the raw water storage ponds at the WTP. (LAFCo,2008; Fort Bragg, July 2017). The aging infrastructure of the water system and the reliability of the water collection conduits are the primary factors influencing the City’s ability to provide water services to customers. | Fair condition/ Upgrades planned/ identified | [5 empty] | Fort Bragg City WWTP; Expedited Payment Letter | 2017-06-16 | sewer | The City public water system includes raw water collection,treatment, and distribution facilities,which are owned and operated by the City. The Water Treatment Plant(WTP)is located at 31301 Cedar Street in Fort Bragg. | Adequate | The priority storm drain improvements in the 2004 Storm Drainage Master Plan have been implemented. Much of the area north of Pudding Creekand south of the Noyo River generally do not have improved drainage systems in place. Drainage in these areas is generally throughnatural channelsor site installed drainage pipes.Chapter 12.14, 17.60 and 18.60 of the City's Municipal Code require the City to reviewand conditionnew development to ensure that adequate on-site and off-site drainage is included in the development.New development is required to paya drainage impact fee and therebyfund improvements necessary to ensure adequate capacity within the storm drain system. (Fort Bragg, 2012c; Fort Bragg, July 2017) |  |  | 1
| y | 1 | FORT JONES, TOWN OF | City | P.O. BOX 40, FORT JONES, CA 96032 | n | y |  | 366 | monthly/ annual flate rate | Familiar; not a participant | [5 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  | 1 |  | Town of Fort Jones | Siskiyou | North Coast, Region 1 | 45365 | n | 675 | GW | Wells (3) |  | 3 | 35 min./water 15 sewer | $51 - $100
| y | 1 | GARBERVILLE SANITARY DISTRICT | Sanitary Dist | P.O. BOX 211 GARBERVILLE, CA 95542 | y | y |  | 442 |  | Familiar; infrequent participation | Unfunded |  |  |  |  | 1 | 1 | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  | Garberville , Humboldt | Humboldt | North Coast, Region 1 | 36371 | n | 1500 | SW | Instream - Eel River, Well |  | 1 | residential water - 66.89 residential wastewater - 47.70 Water- Variable Base and Variable Usage base rate is by meter size and usage rate is by amount used. Wastewater - fixed base and variable usage. residential usage based on the months of Jan-Mar. Commercial base rate based on 90% of last years usage and usage rate based on 90% of last months usage for each strength. | $101 - $150 | The water treatment facility produces water that meets or exceeds the State regulations for drinking water. The turbidity and residual free chlorine levels comply with the maximum allowable levels, treatment occurs in highly efficient chlorine contact chamber. | Presently, the District maintains and operates a water system and a sewer system. The water system was recently purchased from private owners and consists of two water sources, a treatment plant, four water tanks, three booster stations, approximately 380 active service connections, and a waterline distribution network. One of the water sources is surface water from the South Fork of the Eel River and one is a shallow well in downtown Garberville. The surface water source is regulated by the California Surface Water Treatment Regulations. The existing system has adequate production, treatment, and storage capacities for the average daily demand. The maximum daily demand is 370,830 gpd based upon the maximum month of July 1999. The total storage capacity for the system is approximately 300,000 gallons. This is not sufficient to meet the maximum daily demand or to provide any fire protection services during the maximum daily demand. The existing system provides adequate water pressure throughout the District. Reports of inadequate flow for fire suppression purposes have been received for Maple Street. This is likely due to insufficient line sizes. The system in general has very few fire hydrants, and many of those installed are wharf hydrants that will not provide sufficient flow for fire suppression. The fire department reported that there are only a few hydrants that are approved for use during a structure fire, and most are located on Redwood Drive. The Eel River Infiltration Gallery is the main water source and it is a surface water source. It was originally installed in 1940. The infiltration gallery has one 6-inch 320-gpm 50-HP submersible pump that was installed in February 1999. The pump operates against an approximate 380 feet differential elevation head. The pump discharges to the water treatment plant adjacent to the 200,000-gallon storage tank. The pressure filter in the water treatment plant has a limited capacity of 250 gpm. The existing treatment plant filtration cell does not have sufficient capacity to allow processing of the maximum daily demand. The treatment plant produced a total of 80 million gallons of water in 1999. The majority of the water mains in downtown Garberville were installed prior to 1940. Some of the lines are lead joint, some are copper, and most are either iron or asbestos cement. Only the line in Redwood Drive is 8 inch. Most of the downtown mains are 4-inch lines. The water mains in the Wallen and Johnson Subdivision were installed in 1978 and are mostly 6-inch lines. The Garberville SD recently completed a water system improvement project that included: new submersible river intake pumps and emergency power supply; a new surface water treatment plant with new pressure filters, highly efficient chlorine contact chamber, and a backwash water recycling system; the retrofit of an existing booster pump station with new pumps, valving, and controls; over one mile of new water mains and distribution piping; and a new 750,000 gallon finished water storage tank. In addition, the Garberville SD recently annexed 84 Assessor’s Parcels already served by the District, into the district boundary. According to the Local Agency Formation Commission (LAFCo) staff report for the annexation, “The District has been actively planning and constructing water and wastewater facility improvements to address system deficiencies and to provide sufficient capacity to meet current and future service demands.” | Fair condition/ Upgrades planned/ identified | [7 empty] | sewer | The Garberville SD wastewater system consists of a collection system with lift stations to convey wastewater to a central treatment facility. In 2011, the District completed a major treatment plant upgrade to address capacity limitation and a RWQCB cease and desist order. The $3.5 million project included: three oxidation ponds, four wetland treatment ponds, chlorination via an onsite chlorine generation system, improved percolation ponds, and an onsite operation and maintenance building. The first primary oxidation pond was constructed at a new location. The other oxidation ponds and the wetland treatment ponds were created by modifying the existing treatment ponds and recharge basin. Improvements to the percolation ponds consisted of cleaning and re-grading each basin. In November 2011, the Water Quality Control Board rescinded the cease and desist order and issued a new Waste Discharge Permit (ID# 1B831200HUM) for the treatment plant. This waste discharge permit contains guidelines for an average dry weather flow of 162,000 gpd and a peak wet weather flow of 235,000 gpd. The treatment plant is currently operating at 38.88% of the capacity during dry weather flows. | Good condition
y |  | 1 | GASQUET C.S.D. | CSD | P.O. BOX 86 GASQUET, CA 95543 | y | y | y | 210 | uniform rate schedule | Familiar; infrequent participation | Unfunded | 3 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 0 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | Gasquet, CA | Del Norte | North Coast, Region 1 | 35769 | n | 775 | SW | Instream - North Fork Smith River |  |  | 0-50 | $0 - $50 | Raw water is pumped by the Gasquet CSD from the Smith River to a water treatment plant located approximately 500 feet from the river. Upon treatment, the water enters into a distribution system comprised of 6-inch, 8-inch and 4-inch mainlines, which has metered connections. There are two storage tanks, which total 350,000 gallons of storage.The Gasquet CSD’s existing water system, originally constructed in the late 1960s, has been modified somewhat over the years. The water system includes the following infrastructure:oTwo 5 horsepower (hp) submersible pumps; oTwo 3 hp submersible pumps; o6-inch, 8-inch,and 4-inch water distribution line throughout service area;oTwo storage tanks (150,000 and 200,000 gallons); andoWater Treatment Plant:-Two adsorption clarifiers; -Four 5,000 gallon contact tanks; -6,000 gallon “old” adsorption clarifier (serves as a contact tank);-Two 1,200 gallon “wet well” tanks;-Four booster pumps (7.5 hp, 10 hp, 15 hp, and 20 hp); and-Pressure and sand filter. | The District receives surface water from the Smith River at the confluence of the North Fork and Middle Fork. The District holds a Water Rights Permit to take up to 345 gallons per minute (gpm), with an annual withdraw limit of 135.9 million gallons (417 acre-feet). Raw water is pumped by the Gasquet CSD from the Smith River to a water treatment plant located approximately 500 feet from the river. Upon treatment, the water enters into a distribution system comprised of 6-inch, 8-inch and 4-inch mainlines, which has metered connections. There are two storage tanks, which total 350,000 gallons of storage.The Gasquet CSD’s existing water system, originally constructed in the late 1960s, has been modified somewhat over the years. The existing water delivery system is adequate to serve the Gasquet community. As water demand grows, the water treatment system is approaching its treatment capacity. Capacity challenges were documented in the District’s 2009 Water Treatment Plant Capacity Report and are summarized above. Some of the WTPCR recommendations have been implemented; other portions are currently being, or are scheduled for, implementation. Replacements and upgrades occur as needed. The District did not identify any immediate infrastructure needs at this time. | Adequate | [7 empty] | septic | about 352 households and one commercial | Adequate
|  | 1 | GEYSERVILLE SANITATION ZONE | Public Utility | 155 HAMILTON LANE, GEYSERVILLE, CA (Mailing:) 404 Aviation Blvd., Santa Rosa, CA 95403 | [19 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | The Geyserville Sanitation Zone (Geyserville SZ) service area covers approximately 177 acres.Physical address, 155 Hamilton Lane, Geyserville, APN 140-080-022.The Geyserville SZ provides service to approximately 318 parcels using a gravity collection system and treats wastewater from approximately 405 ESDs. | Sonoma | North Coast, Region 1 | 46250 | n | 862 | [16 empty] | sewer
|  | 1 | GILL CREEK MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 46250 | n
|  | 1 | GOLDEN BEAR RV PARK | Other | Del Norte | [28 empty] | Del Norte |  | 27200 | n
| y | 1 | Graton CSD | CSD |  | y | y |  | 462 | Monthly/ Annual Flat Rate | Familiar; infrequent participation | Funded | [5 empty] | 1 | [10 empty] | 1 |  |  |  |  | Sonoma | North Coast, Region 1 | 74355 | n | 1300 | UNK |  |  |  | There is a one-time connection fee of $10,352, and an annual fee of $1,574.37. | $101 - $150
| y | 1 | GRATON MUTUAL (GREEN VALLEY HOA) | Mutual |  | n | n |  | 0-25 | Monthly/ Annual Flat Rate | Unfamiliar; disinterested | [22 empty] | Sonoma | North Coast, Region 1 | 71576 | n | 0-50 |  |  |  |  | $50-100 | $51 - $100
|  | 1 | GREEN ACRES TRAILER PARK | Mutual | [29 empty] | Mendocino | North Coast, Region 1 | 31027 | n
y | y | 1 | GRENADA SANITARY DISTRICT | Sanitary Dist | P.O. Box 415 GRENADA, CA 96038 | y | y | y | 103 | Monthly/ annual flat rate; Increasing block (graduated) rate schedule | Unfamiliar; disinterested |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Grenada, CA | Siskiyou | North Coast, Region 1 | 43523 | n | 280 | GW | Well (1) | 1 |  | 51-100 | $51 - $100 |  |  |  |  | 0 | 1. Failure to collect repeat and raw source coliform bacteria samples. | 2. 9/6/17 |  |  |  | sewer
|  | 1 | Gualala Community Services District | CSD | 8851 California Hwy 1, Gualala, CA 95445 | y |  |  | 428 | graduated | [22 empty] | Gualala, CA | Mendocino | North Coast, Region 1 | 40185 | n | 750 | [17 empty] | The District provides collection, treatment, and disposal of wastewater generated by hookups within the service area and maintenance of related facilities and equipment services. Wastewater is treated to a tertiary level. To achieve the tertiary level of treatment, the District utilizes an extended aeration activated sludge plant with clarification and Title 22 Sand Filter and Disinfection method. The Wastewater Treatment Plant is a Step System. The waste solids are disposed of at a solids disposal site and the treated effluent is used to irrigate the Sea Ranch Golf Links. Using GCSD’s reclaimed water at the golf course is beneficial because the North Coast Regional Water Quality Control Board (RWQCB) indicates that wastewater effluent cannot be discharged directly to a ditch, creek, or stream. This is to protect sensitive natural resources within these types of drainages. Wastewater is collected within the GCSD boundaries in Mendocino County and transported for treatment at the District’s facility, which is located in Sonoma County. Each parcel has its own interceptor tank. Heavy rain in the area required a design for extended effluent storage during the winter season. The State Water Resources Control Board (SWRCB) took particular interest, and recommended that the plant be located in Sonoma County partially as a reclamation facility for the Sea Ranch development and golf course. Authorities felt that this recommendation would reduce and offset freshwater demands on the environmentally sensitive Gualala River. The wastewater system was designed to serve existing development and provide for additional growth within the GCSD Sewer Assessment District boundaries. All new development within Zones 1 and 2 must connect to the wastewater treatment system. The GCSD owns 15.47 acres of land on which the treatment plant is located. The parcel is located in Sonoma County (Assessor’s parcel number 122-040-010) and contains the wastewater treatment plant, a maintenance garage, office trailer, and lab. | Good condition
|  | 1 | HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 71576 | n
| y | 1 | HAPPY CAMP C.S.D. | CSD | P.O. BOX 1129 HAPPY CAMP, CA 96039 |  | y |  | 453 | Uniform Rate Schedule | Familiar; infrequent participation | Funded | [10 empty] | 1 |  |  | 1 | 1 |  | 1 | 1 |  |  | Happy Camp, CA | Siskiyou | North Coast, Region 1 | 41000 | n | 1100 | SW | Instream - Elk Creek |  |  | 0-50 | $0 - $50
| y | 1 | HAPPY CAMP S.D. | Sanitary Dist | P O Box 379 HAPPY CAMP, CA 96039 |  | y |  |  | Uniform Rate Schedule | Familiar; infrequent participation | Funded | [10 empty] | 1 |  |  | 1 | 1 |  | 1 | 1 |  |  |  | Siskiyou | North Coast, Region 1 | 41000 | n | [5 empty] | 0-50 | $0 - $50
|  | 1 | HAWKINS WATER CO-CAL WATER SERVICE (PUC) | Public Utility | 1720 NORTH FIRST STREET SAN JOSE, CA 95112 |  |  |  | 51 | [24 empty] | Sonoma | North Coast, Region 1 | 61576 | n | 138 |  | well (2) | 2
y |  | 1 | HEALDSBURG, CITY OF | City | 401 GROVE STREET HEALDSBURG, CA 95448 | y | n |  | 4516 | [15 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 2 |  | Healdsburg, CA | Sonoma | North Coast, Region 1 | 57639 | n | 13501 | GU | well (14) |  |  |  |  | Before entering the water distribution system, the water is chemically treated and ultra-filtered to improve its quality and remove most contaminants. The water is then stored at various locations throughout the City, ready to be delivered to our homes and businesses. | [9 empty] | sewer
|  | 1 | HEIGHTS MUTUAL WATER COMPANY | Mutual | PO. BOX 58 FULTON, CA 95439 |  |  |  | 110 | [24 empty] | Sonoma | North Coast, Region 1 | 42958 | n | 363 | GW | Well (3)
| y | 1 | HERITAGE HOUSE RESORT AND SURFWOOD MUTUAL WATER CORP. | Mutual | [28 empty] | HERITAGE HOUSE RESORT/SURFWOOD RESIDENTS | Mendocino | North Coast, Region 1 | 31027 | n
y | y | 1 | HILLS RANCH MUTUAL WATER COMPANY | Mutual | P.O. BOX 411 ALBION, CA 95410 | n | n | n | 48 | Monthly/ annual flat rate, Increasing block (graduated) rate schedule, tiered for water useage | Familiar; lack resources to participate |  | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | Hills Ranch Road, Mendocino, CA | Mendocino | North Coast, Region 1 | 39667 | n | 60 | GW | Wells (4) |  |  | Average service fees range between $81 and $100 per month. | $51 - $100 | The Company owns and maintains 4active wells and approximately 2miles of pipeline, a 200,000 gallontank,and 3chemical feed pumps. The Fire District owns a tank of 100,000 gallons capacity,which is operated by the Company as an integral part of its water supply system. In additionto providing waterto the Fire Districtfor fire protection the Company has in thepastsupported the school district when their water supply failed andthe Town of Mendocino during a period of severe drought. | In 2014 the Company was placed under the groundwater use regulations of Mendocino City Community Services District (MCCSD), which are susceptible to restrictions during time of droughts. The Company is exploring reactivation of its surface water sources in Slaughterhouse Creek as a means of resolution to the issue. A connection with the Surfwood Mutual Water Corporation is another possibility the Company is considering, as is a connection to a potential citywide water supply system should MCCSD undertake to develop one. Further challenges noted by the Company include improving water quality, upgrading their plant, installing an additional fire hydrant, responding to disasters such as earthquakes, and replacing tanks. | Poor condition | Excessive storage, some customer complaints about water quality and taste | [10 empty] | 1
|  | 1 | HILTON MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 49732 | n
| y | 1 | HOLLAND HEIGHTS MUTUAL WATER COMPANY | Mutual |  | n | n |  | 100-250 | Increasing Block (Graduated) Rate Schedule | Unfamiliar; disinterested | [6 empty] | 1 | [5 empty] | 1 |  | 1 | [5 empty] | 1 | We serve the Holland Heights Neighborhood, adjacent to Santa Rosa in Sonoma County | Sonoma | North Coast, Region 1 | 46037 | n | 250-500 |  |  |  |  | $0-50 | $0 - $50
y | y | 1 | HOLLY RANCH VILLAGE | other | 32400 Creekside Lane, Fort Bragg, CA 95437 | y | n | y | 13 | monthly/ annual flat rate | Familiar; lack resources to participate |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 33300 Lassen Road, Fort Bragg, CA | Mendocino | North Coast, Region 1 | 39667 | n | 50 | GW | Wells (2) |  |  | part of rent
y | y | 1 | HOPLAND PUBLIC UTILITY DISTRICT | PUD | 151 LAWS AVENUE UKIAH, CA 95482 | n | n | y | 350 | Uniform rate schedule | Familiar; infrequent participation | Unfunded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | Hopland, CA | Mendocino | North Coast, Region 1 | 19356 | n | 1069 | GW | Wells (2) |  |  | 100-150 | $101 - $150 |  | The HPUD serves 350 water customers but has no water rights. The HPUD maintains two storage tanks with a capacity of 800,000 gallons, which is approximately half the summer supply. Current demand is 350 AFY. The HPUD contracts with RRFC for up to 400 AF of Lake Mendocino water. The HPUD has sufficient water capacity. The Ukiah Valley Special Districts Municipal Service Review of 2013 recommended that Willow CWD, Calpella CWD, and Hopland PUD consider a formal consolidations through LAFCO. | Adequate | [7 empty] | sewer | [5 empty] | 1
|  | 1 | HORNBROOK C.S.D. | CSD | P.O. Box 29 HORNBROOK, CA 96044 |  |  |  | 147 | [24 empty] | Siskiyou | North Coast, Region 1 | 33000 | n | 280 | SW | Instream plus wells (3) | [8 empty] | 0 | 1. Failure to conduct routine monitoring for coliform bacteria in drinking water | 1. 1/20/2016
| y | 1 | Hussey Ranch Corporation (HRC) C.S.D. | CSD | 159 CLUB DRIVE CRESCENT CITY, CA 95531 | no | n |  | 51 | Monthly/ Annual Flat Rate | Familiar; not a participant | [21 empty] | Some unincorporated areas of Del Norte County. | Del Norte | North Coast, Region 1 | 26544 | n | 150 | GW | Well |  |  | 30 | $0 - $50 |  | The HRC CSD gets its water from a well on Peacock Ranch, located adjacent to the Smith River, which provides water to residential users and the Del Norte Golf Course. The State Department of Health Services classifies the HRC CSD’s source water as groundwater. The classification of water source type dictates the water system regulations to ensure water quality. The district has a 132,000 gallon storage tank and distribution piping. The system has a maximum capacity of approximately 100 connections. The HRC CSD’s overall water system is in good condition. The existing system has no major deficiencies for serving the current population. Due to age and composition the existing poly piping serving homes around the golf course is in need of replacement and should be scheduled. In addition to the Peacock Ranch operation, two small privately owned water systems are in use. The Kelsey Trail Water Company, located in the northeast corner of the HRC CSD SOI between North Bank Road and the Smith River, serves residential users. The second privately ownedsystem, Blackberry Water Company, located in the southern portion of the HRC CSD SOI between North Bank Road and Smith River, serves the immediately surrounding residential area.The Jedediah Smith Homeowners Association (JSHOA) board members and residents have inquired about connecting their water system with the HRC CSD. The JS HOA is located just north of the district boundaries and in the sphere of influence. The HRCCSD responded that if the JSHOA is willing to provide additional infrastructure needed to compensate for the new system demand a connection could be considered. HRCCSD requested that JSHOA get an independent evaluation to address technical issues in each system. | Adequate
y |  | 1 | HUCKLEBERRY MUTUAL WATER COMPANY | Mutual | 5514 Doyle Street EMERYVILLE, CA 94608 | y | y | n | 29 | monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 0 | 3 | 3 | 3 | 3 | 0 | 1 | 2 | 0 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 1 | 2 | 3 |  | Huckleberry Community in Cazadero, CA | Sonoma | North Coast, Region 1 | 35000 | n | 45 | GW | Well |  |  | 51-100 | $51 - $100 |  |  |  |  | A | 1. Total coliform MCL violation for August 2013 | 1. 9/30/13 | [7 empty] | 1
y | y | 1 | HUMBOLDT BAY MWD | Municipal Water Dist | Municipal Water Dist | y | y | y | 209 | Increasing block (graduated) rate schedule | Familiar; regular participant | Funded | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | greater Humboldt Bay area - including the cities of Eureka, Arcata and Blue Lake, as well as Community Service Districts serving unincorporated areas such as McKinleyville, Cutten, Fairhaven, Fieldbrook and Manila. The population served via these agencies totals about 65,000 people. | Humboldt | North Coast, Region 1 | 20346 | n | 65000 | GW | Wells (5) |  |  | 0-50 | $0 - $50 | Drinking water delivered by the district is drawn from wells located in the bed of the Mad River northeast of Arcata. These Ranney Wells, draw water from the sands and gravel of the riverbed at depths of 60 to 90 feet, thereby providing a natural filtration process. In the summer this naturally filtered water is disinfected with chlorine and delivered to the District’s wholesale municipal and retail customers in the Humboldt Bay Area. In the winter the water is further treated at a regional Turbidity Reduction Facility which reduces the occasional turbidity (cloudiness) in the District’s source water. The District’s source water has been classified by the DHS as groundwater. A groundwater classification dictates the regulations that a water system must follow to ensure water quality. | [7 empty] | 1. Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Woodley Island Marina, WDID NO. 1 12I019820 2. Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Redwood Terminal 2, SCDC No. 1 12I025990 3. Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Fields Landing Boat Yard, WDID No. 1 12I019819 4. 2nd Noncompliance: Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Fields Landing Boat Yard, WDID No. 1 12I019819 5. Water Quality Certification For HBMWD - Mad River Operations 6. Water Quality Certification for HBMWD - RW Mathews Dam/ Ruth Lake Operations | 1. 8/4/16 2. 8/4/16 3. 8/4/16 4. 9/12/16 5. 9/15/15 6. 9/15/15
y | y | 1 | HUMBOLDT C.S.D. | CSD | Humboldt CSD P.O. Box 158 CUTTEN, CA 95534 | y | y | y | 7714 | uniform rate schedule | Familiar; lack resources to participate | Unfunded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 2 | Outside Eureka City limits | Humboldt | North Coast, Region 1 | 44257 | n | 22842 | GW | CC - Humboldt Bay MSD - Purchased, wells (2) |  |  | 51-100 | $51 - $100 | Water for the Humboldt CSD system is provided by the Humboldt Bay Municipal Water District (HBMWD) and three wells located in the Humboldt Hill area. HBMWD has sufficient water supply to meet the demands of Humboldt CSD and its other municipal customers, and Humboldt CSD has extensive available capacity within District wells. | There are no significant deficiencies within Humboldt CSD’s water system, although some storage and fire flow improvements are anticipated. Water service within Humboldt CSD is generally very good. The District purchases approximately 33% of its potable water from the Humboldt Bay Municipal Water District. 34% of the district’s water is provided from District owned wells located at the base of Humboldt Hill and Spruce Point area. These wells primarily serve Humboldt Hill, Fields Landing, King Salmon, College of the Redwoods, and some portions of the Pine Hill area. The Humboldt CSD UWMP indicates that water depths in the wells (installed in 1988) are not influenced by climatic variation and not susceptible to drought conditions (Humboldt CSD UWMP 2015, Page 14). The District also has a long term contract with the City of Eureka to purchase additional water (34% of total demand), which also originates from Humboldt Bay Municipal Water District. The district and City’s water systems are interconnected at various locations allowing for such transfers to occur. Humboldt CSD supplies water to 7,698 active connections (HCSD 2015 SWRCB Annual Report), approximately 97% of which are residential. Humboldt CSD’s water system in Freshwater is in good condition overall. There are no major infrastructure deficiencies associated with the existing system. Water service within Humboldt Hill is generally very good. The District has an ongoing program for upsizing undersized water mains installed to improve fire protection. Myrtletown’s water system is in good condition overall. There are no major infrastructure deficiencies associated with the existing system. Humboldt CSD is replacing older steel pipe in the distribution system as funding is available. Humboldt CSD’s South Eureka water system is in good condition overall. There are no major infrastructure deficiencies associated with the existing water system. Some older steel pipe in the distribution system is currently being replaced and additional water storage capacity is planned to support planned growth and improve fire protection. | Fair condition/ Upgrades planned/ identified | [7 empty] | sewer | Humboldt CSD operates a wastewater collection system that interconnects with the City of Eureka collection system and the City’s Elk River Wastewater Treatment Plant (WWTP). Portions of the Humboldt CSD and City of Eureka collection systems experience inflow and infiltration (I&I) of rainwater and are near or at capacity in a number of locations during significant rain events. Although extreme wet weather flows approach the design capacity of the WWTP, the plant is designed to treat all flows that the collection system conveys in its current configuration and with the current peaking factor. The City is conducting a study of the Elk River WWTP infrastructure to identify hydraulic and process “bottlenecks” and proposes cost effective improvements to increase capacity, rather than construct a total plant expansion. The City expects that this strategy will allow step-wise increases in WWTP capacity that keep pace with development within the Humboldt CSD and the City of Eureka over the next 20 years. The City of Eureka and Humboldt CSD cooperatively worked on the Martin Slough Interceptor Project to address the collection system capacity issues. The Martin Slough project is multipurpose in function, including reducing wastewater overflows that degrade the environment, eliminating existing City and Humboldt CSD wastewater lift stations (by conversion to gravity service), improve energy conservation, and provide capacity for planned development. The Martin Slough Interceptor was put in service in November of 2014. The Martin Slough project boundaries include areas within the City of Eureka that will gravity flow into the proposed interceptor, and portions of the unincorporated area surrounding Eureka that can utilize the interceptor based on proximity and topography located within the urban limit line established by the Eureka Community Plan and the Humboldt Bay Area Plan. Portions of the South Eureka area which include Bayview, Pine Hill, Rosewood, Cutten and Ridgewood are not within the Martin Slough project boundaries. Wastewater within these areas drains to portions of the City of Eureka collection system other than the Martin Slough Interceptor. | Fair condition/ Upgrades planned/ identified
|  | 1 | Humboldt County RID #1, Shelter Cove POTW | Resort Imp Dist | 9126 Shelter Cove Drive, Shelter Cove, CA |  |  |  | 620 | [24 empty] | Humboldt | North Coast, Region 1 | 42118 | n | 1500 | SW | Instream - Telegraph Creek - raw, SP - springs - raw, wells (17)
y | y | 1 | HUNTER VALLEY CSD | CSD | 25 Del Ponte Drive, Klamath, CA 95548 | n | N | Y | 65 | monthly/ annual flat rate | Familiar; infrequent participation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Hunter Creek Sub-division, Klamath, CA | Del Norte | North Coast, Region 1 | 27200 | n | 178 | GW | Well (1) |  |  | $16 per month billed annually | $0 - $50 | Hunter Valley Community Services District supplies clear, sanitary, tasteless and odorless drinking water to 64 member customers with a capacity for a total of 80 properties within the HVCSD Jurisdiction at 50 to 60 PSI. The District sanitizes the water system once per month with chlorine using a drip monitor. | HVCSD’s water source is a single well located adjacent to Hunter Creek. Total District water use is metered, however individual residential connections are not. Water is supplied to homes through 1” PVC supply lines on an unlimited basis. HVCSD’s water system is operating at 85% of its service capacity. The water system adequately serves the existing connections with no major deficiencies, however, the system is operating near its capacity. Also, in light of current statewide drought conditions HVCSD should consider metering all connections within the District. | Fair condition/ Upgrades planned/ identified | [7 empty] | septic | all residents on own septic | Adequate
|  | 1 | HYDESVILLE CO. W.D. | Water Dist | Humboldt | [5 empty] | Familiar; infrequent participation | Unfunded | [21 empty] | Humboldt |  | 56042 | n | [7 empty] | The water is chlorinated at the well site and then pumped to the District’s two storage tanks | The District’s water supply is obtained from two (2), twelve inch (12”) wells located on District owned land near Yager Creek. These wells are equipped with pumps which are rated at a total of approximately 359 gpm. The water is chlorinated at the well site and then pumped to the District’s two storage tanks. These storage tanks have a capacity of 200,000 and 400,000 gallons, which is estimated to be the equivalent of seven days of normal usage. The stored water is distributed by gravity, throughout the District’s distribution system. The District has installed fire hydrants throughout the service area. Normal operating procedure for the District is to utilize one well while maintaining their second well in a reserve status, except during peak usage days (estimated to occur five to seven times per year). This is standard procedure which allows for sufficient reserve capacity in case of pump failure of other disruption in the operation of a well. Water service within Hydesville is generally good. The District is at approximately 60% of its source capacity during peak usage periods. In some areas located in the northern part of the District (Quail Hill subdivision area), the 4-inch mainline is inadequate in size to maintain the fire flow requirements and topography is a constraint on service area expansion utilizing the existing gravity fed system. The District is planning to increase the size of distribution lines in the Quail Hill subdivision, and install an additional well and 500,000 gallons storage, as funds become available. | Fair condition/ Upgrades planned/ identified
y | y | 1 | INDIAN CREEK TRAILER PARK | Other | P.O. BOX 8 DOUGLAS CITY, CA 96024 | y | y | y | 35 | monthly/ annual flat rate |  |  | 2 | 1 | n/a | 0 | 3 | 3 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 0 | 1 | 0 | 3 | 1 | 59680 Hwy 299 west Douglas City, CA 96024 | Trinity | North Coast, Region 1 | 50313 | n | 121 | SW | Instream - Indian Creek Infiltration Gallery |  |  | 0-50 | $0 - $50 |  |  |  | coliform and e coli according to the LT2 sampling. Some possible pesticides from marijuana growers up stream.** We do not detect any of these after water is through the treatment plant. | 0 | 1. Citation for failure to submit surface water treatment monthly monitoring reports | 1. 3/1/2017 |  |  |  | septic | Septic system with no treatment | Adequate
|  | 1 | IRISH BEACH WATER DISTRICT | Water Dist | P.O. Box 67 MANCHESTER, CA 95459 15401 Forest View Road, Manchester, CA 95459 | y |  |  | 201 |  | Unfamiliar; lack resources to investigate/participate | [21 empty] | Irish Beach | Mendocino | North Coast, Region 1 | 48828 | n | 560 | SW | Instream Irish Gulch Lower Intake, Upper intake, wells (2) | [5 empty] | The District has five water tanks strategically located throughout the District (Refer to Figure 5-5). Tank 3 is an 84,000 gallon tank that supplies water to the eastern side of the subdivision and was replaced in 2010. The western side of the subdivision is supplied via Tank 1, which is a 210,000 gallon tank that was replaced in 2013. A 10,000 gallon settling tank is located between the Irish Gulch diversion and treatment facility, which has a design capacity of 42 gpm (0.09 cfs) or 57 gpm (0.127 cfs) with a filter unit kept in reserve.In the 2010–2011, the lower diversion at Irish Gulch was put online, numerous fire hydrants were added throughout the subdivision, water treatment modifications were made, a transfer station was rebuilt, and a pressure reducing station was installed. The District has five water storage facilities, a pipeline network, hydrant system, and a water treatment plant. (Refer to Figure 5-5). The District has approximately 7.6 miles of pipeline, ranging from 6 to 2 inches in diameter. Parts of the District’s distribution system dates from 1965, with sections added over the years, the newest of which was installed in 2000. Over 83 percent of the District’s distribution and transmission system is more than 30 years old. Much of this system has an estimated useful life of 40 years. To address aging infrastructure needs, a Proposition 218 Assessment was passed by District voters in early the 2000s.The assessment funds are kept in a special reserve account specifically for capital improvements including but not limited to replacement of pipelines, pumps, valves, tanks, hydrants, and connections. The District faces a number of challenges including ongoing litigation and identification and development of water sources for future development. Although not an immediate need, the District will need to identify additional sources to provide water supply as buildout of the District nears. Additionally, aging infrastructure is reaching the end of its lifespan and will need to be replaced or repaired in the near future. | Fair condition/ Upgrades planned/ identified | [7 empty] | septic | In 1980 the IBWD passed a Resolution of Intention to form a wastewater disposal zone under Health and Safety Code Sections 6955, et seq. The purpose of the establishment of the zone was to monitor, the maintainance, repair, replacement and pumping of wastewater disposal systems after such systems are initially installed pursuant to County Health and/or Regional Water Quality Control Board permits and standards on properties previously established as building sites within the subdivision known as Irish Beach. The District was not required to go through LAFCo to initiate the zone. As such, the District is responsible for maintaining individual wastewater disposal system records, including date of installation, as-built plans of installed systems and service records of systems. It is also under the purview of the District to send to new owners and owners of new systems information regarding maintenance practices that should be followed and local contractors that provide service. To enforce this, IBWD passed Resolution No. 93-5, which requires that all septic tanks be inspected and/or pumped if necessary every five years by a registered sanitarian or a septic tank operator. In 2011, the District passed Resolution No. 2011-2 to establish discharge limits of waste that may contaminate the waters of the state flowing through Irish Beach. | Adequate
|  | 1 | JACOBY CREEK CSD - combined with City of Arcata | CSD | City of Arcata 736 F Street ARCATA, CA 95521 |  |  |  | 325 | [24 empty] | Humboldt | North Coast, Region 1 | 28277 | n | 913 | GWP | HB MWD purchased | [5 empty] | The Jacoby Creek County Water District is located adjacent to the south-eastern boundary of the City of Arcata and extends along Jacoby Creek in a generally south-east direction for approximately four (4) miles. The present boundaries of the District contain approximately five (5) square miles or 3200 acres. The District's water distribution system was constructed in 1974 with funds obtained from a Davis-Grunsky loan from the State of California. The District obtains its water from the City of Arcata, who in turn, obtain their supply from the Humboldt Bay Municipal Water District. An agreement with the City of Arcata provides for the City to supply water, operate and maintain the distribution system and provide billing and collection services for the District. Water service is currently supplied to 215 connections within the District. Most of these connections are for residential users plus a few small businesses. Jacoby Creek’s water system is in good condition. The biggest deficiency with the existing system is lack of adequate storage capacity. The study area has only about 27% of maximum day demand in storage capacity (Winzler and Kelly, 2008). In addition, some distribution piping within the system is fewer than six inches in diameter and unable to provide adequate fire flows. | Storage capacity insufficient
y | y | 1 | JED SMITH HOMEOWNERS ASSN. | Mutual | 1600 TOLOWA ROAD CRESCENT CITY, CA 95531 | y | y | n | 27 | uniform rate schedule | Unfamiliar; disinterested |  | 3 | 2 | 1 | 0 | 3 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 3 | 0 | 0 | 2 | 1 | 3 | 3 | Jed Smith Homeowners' Association | Del Norte | North Coast, Region 1 | 26544 | n | 58 | GW | Wells (2) |  |  | 51-100 | $51 - $100 |  |  |  | Intermittent E-coli and choliform positive testing results | B | Groundwater under Direct influence of surface water with inadequate treatment | 2017-02-17 | [7 empty] | 1
|  | 1 | JUNIPER CREEK ESTATES | Other | P.O. Box 1108 FORT JONES, CA 96032 |  |  |  | 52 | [24 empty] | Siskiyou | North Coast, Region 1 | 45365 | n | 130 | GW | Well
|  | 1 | KAMP KLAMATH CORP. | Other | Del Norte | [28 empty] | Del Norte |  | 27200 | n
| y | 1 | KELLY MUTUAL WATER COMPANY | Mutual |  | n | n |  | 25-50 | Increasing Block (Graduated) Rate Schedule | Familiar; infrequent participation | Unfunded | [13 empty] | 1 |  |  | 1 |  |  |  | Kelly subdivision, Sonoma County | Sonoma | North Coast, Region 1 | 99141 | n | 100-250 |  |  |  |  | 50-100 | $51 - $100
|  | 1 | KLAMATH C.S.D. (Del Norte Community Development) | CSD | P. O. BOX 430 KLAMATH, CA 95548 | y |  |  | 62 | increasing block | [22 empty] | Klamath | Del Norte | North Coast, Region 1 | 27200 | p | 240 | GW | Wells (3) |  |  | 36/month water; 18.40/ month, sewer | $51 - $100 |  | The Klamath CSD water infrastructure includes three active untreated wells, one 125,000 gallon water storage tank, and a water distribution system. Water is metered and supplied to homes through 3/4” supply lines. The Klamath CSD serves approximately 62 water connections within the District. In 2014 the District hooked up three new commercial facilities to the water system including a hotel/casino, a Yurok Knowledge and Cultural Park, and the Yurok Tribe Justice Center. The water system was designed to meet both domestic water and fire flow requirements. The Klamath CSD’s water system adequately serves the existing connections with no major deficiencies. | Adequate | [7 empty] | sewer | The Klamath CSD is responsible for collection, treatment, and disposal of the community’s wastewater. The present service area consists of commercial and residential areas within the Klamath CSD. The District provides approximately 37 residential and 12 commercial wastewater service connections as of 2015. These numbers have not changed due to a Cease and Desist Order that has been placed on the wastewater system by the North Coast Regional Water Quality Control Board (NCRWQCB) since 2006. The wastewater system is capable of serving a maximum capacity of 49 connections. Existing facilities consist of a gravity collection system and transmission lines including two pumping stations, a package type contact stabilization treatment facility, and a system of leachfields. The wastewater collection system includes 3,000 feet of 8-inch and 1,950 feet of 6-inch Vitrified Clay Pipe (VCP); 10 manholes; two 200 gallon per minute (GPM) lift station pumps and vault; chambered septic tank; two 50 GPM effluent pumps; and sewer forcemain (Yurok Tribe, 2012). The existing wastewater leachfields are located directly west of the Klamath community and U.S. Highway 101, and directly east and in the vicinity of the Klamath River. The leachfield system is on Del Norte County land leased to Klamath CSD for wastewater disposal and is under the jurisdiction of the NCRWQCB. The NCRWQCB will not allow expansion of the system beyond the existing wastewater flows due to its location in the 100-year floodplain. The District is currently working on an engineering plan which will address this issue. The old sewer forcemain was located directly adjacent to the wastewater treatment facility and on the west (wet) side of Hwy 101 was temporarily replaced after 2006 storms and Klamath River flooding washed it out. In 2012, 900 feet of new 4-in HDPE sewer forcemain was installed on the east (dry) side of Hwy 101 and crossing to the west side of the highway in the vicinity of the leachfield system, removing the threat of damage to the forcemain from the Klamath River. Two new leachfields were installed in 2009 to replace leachfield capacity lost to the Klamath River in 2006, one was replaced via Indian Health Services (IHS) funding while the other was replaced via Klamath CSD FEMA funding. Two new effluent pumps and new pump chamber were constructed in 2015 to bring the wastewater system and current operation into compliance with the NCRWQCB. The overall condition of the wastewater collection piping is good according to an Inflow and Infiltration (I/I) Study completed by Graysky Engineering for Klamath CSD in 2009. Average wastewater flows throughout the year are 15,192 gallons per day (GPD) with a range of between 11,500-20,000 GPD. | Good condition
|  | 1 | KLAMATH CAMPER CORRAL | Other | Del Norte | [28 empty] | Del Norte | North Coast, Region 1 | 27200 | n
|  | 1 | KLAMATH RIVER RV PARK | Other | Del Norte | [28 empty] | Del Norte | North Coast, Region 1 | 27200 | n
y |  | 1 | LAKE SHASTINA C.S.D | CSD | 16320 EVERHART DRIVE WEED, CA 96094 | y | y | y | 1272 | monthly/ annual flat rate | Familiar; not a participant |  | 0 | 0 | 0 | 0 | n/a | n/a | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | Lake Shastina Community in Weed, CA | Siskiyou | North Coast, Region 1 | 18125 | n | 2400 | GW | Wells (3) |  |  | 51-100 | $51 - $100 | [10 empty] | sewer | Due to the varied topography of the Lake Shastina area, most of the District is serviced by Sewer Lift Stations which pump to the plant; sewer is 36 a month for improved lots and 3 a month of unimproved | Adequate |  |  |  | 1
|  | 1 | LAKE VIEW MUTUAL WATER CO. | Mutual | 4170 Richey Road, Ukiah, CA 95482 1400 ROAD A REDWOOD VALLEY, CA 95470 |  |  |  | 28 | [24 empty] | Mendocino | North Coast, Region 1 | 60692 | n | 90 | GW | Wells (3) | [5 empty] | The Safe Drinking Water Information System lists several monitoring violations, the latest of which was dated 2017 with compliance achieved September 21, 2017. The USEPA notes a monitoring and reporting violation dated March 2017 with compliance achieved in September 2017. | Fair condition/ Upgrades planned/ identified |  | 0 | 1. Lead and copper monitoring and reporting violation 2. Monitoring and reporting violation | 1. 9/8/17 2. 12/16/13
y | y | 1 | LAS PALMAS MOBILE HOME PARK | other | 2839 F STREET EUREKA, CA 95501 | y | n | n | 84 | monthly/ annual flat rate; included with space rental for mobile homes. | Unfamiliar; disinterested |  | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1775 Northcrest Drive, Crescent City CA 95531 | Del Norte | North Coast, Region 1 | 69732 | n | 120 | GW | wells (2) |  |  | did not provide |  |  |  |  | No | [6 empty] | sewer | consolidated with Crescent City for wastewater | Good condition
y | y | 1 | LAYTONVILLE COUNTY WATER DISTRICT | Water Dist | P.O. BOX 32 LAYTONVILLE, CA 95454 | y | n | y | 397 | uniform rate schedule | Unfamiliar; disinterested |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Laytonville, CA | Mendocino | North Coast, Region 1 | 23315 | p | 1320 | GW | Wells (2) |  |  | 51-100 | $51 - $100 | Coagulation/oxydation to treat arsenic The water treatment process includes oxidation with chlorine via a reaction tank, processing through filter pumps, and the addition of various coagulants and sodium bisulfite to reduce chlorine residue. Treatment with the new arsenic filtration components is also performed. After treatment, water is moved to the distribution system, which includes four storage tanks that connect to the water mains. | LCWD is operated via two separate pressure or distribution zones (the East Zone and the West Zone). The East Zone lies east of Ten Mile Creek, and includes the downtown area of Laytonville, the Laytonville K-12 school facilities, and surrounding areas along a two-mile-plus stretch of Highway 101. The West Zone, where approximately 60 percent of District customers reside, lies west of Ten Mile Creek, and includes the Cahto Indian Rancheria and Casino, as well as adjacent residential neighborhoods located on or adjacent to Branscomb Road. There are approximately 13 miles of water mains that carry water to 2 separate pressure or distribution zones (the East Zone and the West Zone) as shown in Figures 6-11 and 6-12. The East Zone lies east of Ten Mile Creek and includes two storage tanks that have a combined capacity of 750,000 gallons. The West Zone lies west of Ten Mile Creek and has two storage tanks with a combined capacity of 310,000 gallons. All four tanks, with a combined capacity of 1,060,000 gallons, are filled through the distribution system. | Good condition | Water quality is an important component of water supply. LCWD reports that water quality is currently very good and it has worked diligently to resolve past water quality issues. For the purposes of transparency, those past water quality issues are summarized here. The U. S. Geologic Survey in 1986 reported that chemical quality of water in basement rocks and valley fill is generally acceptable for most uses. Some wells may have naturally occurring high iron, arsenic, or manganese levels. The Environmental Working Group reported in 2009 that levels of manganese and arsenic exceeded adopted health limits. Additionally other constituents including total haloacetic acids, total trihalomethanes, dibromochloromethane, bromodichloromethane, bromoform, chloroform, alpha particle activity, dichloracetic acid, and radium 228 were noted. Some of these constituents are byproducts of water treatment and distribution and the District received violation notices from the State Department of Public Health CDPH) i n 2006 and 2008. The District has refined its practices to reduce byproducts and is now in compliance with standards for these constituents. The District also treats its water to lower the levels of naturally-occurring iron, manganese, and arsenic in the system. Iron and manganese in treated water do not pose a health hazard; however, arsenic in well water is a human health hazard. When the arsenic standard was lowered to 0.010 milligrams per liter in January 2006, the District was out of compliance and received notice of violation from the CDPH in 2006. The new arsenic treatment system was installed in 2008 and successfully operated in 2009. The District continues to monitor this constituent to ensure compliance with regulatory standards. In December 2009, the District updated its permit application with the CDPH to acknowledge the installation of its new arsenic treatment plant. However, those Valley residents who live outside the District boundaries and utilize their own private water wells as their primary drinking water supply do not benefit from the District’s water treatment process and remain at risk of exposure to arsenic. This is an issue that may need to be addressed with the County Environmental Health Department. A related water quality issue is the presence of hundreds of septic tanks near the ground surface and above the aquifer. Since the community of Laytonville does not have access to a formal centralized wastewater treatment system, septic tanks serve as the primary treatment and disposal method. Sometimes aging septic tanks can fail and create water quality problems such as E coli contamination. Mendocino County is aware of the issues and the Council of Governments (MCOG) and Municipal Council have developed a community plan for Laytonville to start discussing solutions.Protecting water quality is important to LCWD and it has conducted an assessment of Well 1 called a Drinking Water Source Assessment and Protection (DWSAP) Program, as managed by the CDPH. This Assessment found that a potential source of contamination for Well 1 is the rodeo restroom leach field, located adjacent to the WTP. The closed Well 2 also represents a potential source of contamination to Well 1. The District has not yet conducted a Drinking Water Source Assessment and Protection Program for Well 3 and this is a to-do item for the District. | [6 empty] | septic | individual septic systems - 100s near ground surface and above aquifer which supplies LCWD | Regulatory - septic |  | 1
|  | 1 | LEISURE MOBILE HOME PARK | Other | [29 empty] | Sonoma | North Coast, Region 1 | 54497 | n
y |  | 1 | LEWISTON Community Services District | CSD | P.O. BOX 101 LEWISTON, CA 96052 | y | y | n | 49 | uniform rate schedule | Familiar; regular participant | Funded | 2 | 1 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Lewiston, CA | Trinity | North Coast, Region 1 | 30000 | n | 250 | SW | New downstream intake (2015) - raw |  |  | On average, it's about $46/month for water and $54 for wastewater | $51 - $100 | Arsenic was a problem with prior source, but since the new WTP was constructed, it's not a problem. | [14 empty] | 1
|  | 1 | LITTLE LAKE MOBILE HOME PARK | Other | 1500 BAECHTEL ROAD WILLITS, CA 95490 |  |  |  | 19 | [24 empty] | Mendocino | North Coast, Region 1 | 32667 | n | 40 | GW | Well
y | y | 1 | LOLETA C.S.D. | CSD | P.O. BOX 236 LOLETA, CA 95551 | y | y | y | 280 | uniform rate schedule; water: monthly fee + uniform volume rate wastewater: annual fee based on use type | Familiar; infrequent participation | Unfunded | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | Loleta, CA | Humboldt | North Coast, Region 1 | 46458 | n | 750 | GW | Well (2) |  |  | water $45/mo.; wastewater: $47/mo. (569/yr: SFR) | $51 - $100 | The District operates two wells located on Peugh Road in Loleta. Water is pumped from the wells through a Green Sand filter where the iron and manganese is removed by injecting chlorine and potassium permanganate. | Treated water is provided to the service area through approximately 4.5 miles of pipe and to a 225,000 gallon storage tank located just off the freeway. The treatment system runs an average of twelve to thirteen hours a day. One of the wells located on Peugh Road pumps on the average of 60,000 gallons of water a day. Development of the other well is currently in progress. The capacity of the new well is designed to produce 309,600 gallons per day (gpd). It should be noted that most of the Loleta area generally have low yields and water quality issues. With the new well producing the designed capacity, the capacity of water production for the Loleta water system will be 369,600 gpd; this is the ideal production rate, the target water production rate is 144,000 gpd. The storage capacity of the Loleta System is 225,000 gallons, which translates to approximately 1.4 days storage (according to the peak daily usage data). A current estimation of peak usage of the system is 157,000 gpd. According to the designed water production, and including the storage capacity of the system’s 225,000 gallon tank, the Loleta water system is at 26 percent capacity on the highest use day of the year. However, these numbers do not take fire suppression in to consideration, and they are based on the assumption that the facilities are in perfect running order. The District serves 226 homes, 11 businesses, and 2 industrial sites. Due to poor water quality, the Loleta CSD received funding from USDA as well as American Recovery and Reinvestment Act funding, to construct an improvement project that included a new well, transmission line, and treatment plant. The water system improvements are on-line and are sized to serve existing development and currently planned development. According to the LAFCo Municipal Services Review (2008) “the Loleta water system is at 26 percent capacity on the highest use day of the year. However, these numbers do not take fire suppression into consideration, and they are based on the assumption that the facilities are in perfect running order. The District believes that they can supply an additional 60-70 (40 to 50 based on Building Permit data as of 2016) homes.” | Good condition | [5 empty] | Admin Civil Liability | 2018.04.24 | sewer | The District currently relies on percolation ponds for the disposal of treated effluent. This form of disposal is becoming increasingly difficult to permit due to stringent regulations governing disposal to the Eel River during the discharge prohibition period. Other communities such as Rio Dell and Ferndale are being required by the NCRWQCB to find alternative methods of disposal. The District has significant problems with I&I within their collection system, and is operating its wastewater system under a cease and desist order (R1-2015-008) due primarily to excessive I&I. The cease and desist order prohibits additional influent from new or increased connections by the Loleta CSD, except from building permits approved before March 12, 2015. Where the peaking factor has been reduced to 5.5, the Loleta CSD may request to connect additional new or expansion of existing connections provided the additional flows are off-set by a reduction of I&I by at least 2:1 to the collection system. The Loleta CSD is required to complete repairs and upgrades to the system to address this problem by 2019. The Loleta CSD submitted a notice of exemption to the State Clearing House (SCH 2016118314) in November of 2016 for a project to rehabilitate approximately 4,000 feet of sewer main, lateral connections, and a man hole to reduce peak wastewater flows and improve treatment efficiency. | Fair condition/ Upgrades planned/ identified
|  | 1 | LONE PINE MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 99141 | n
|  | 1 | MACDOEL WATERWORKS | Other | 630 NORTH FIFTH STREET KLAMATH FALLS, CA 97601 |  |  |  | 18 | [24 empty] | Siskiyou | North Coast, Region 1 | 28500 | n | 35 | GW | Well
| y | 1 | MADRONA MANOR 140330 | other |  | y | n |  | 0-25 | Monthly/ Annual Flat Rate | Unfamiliar; disinterested | [15 empty] | 1 |  | 1 |  |  | 1 | Healdsburg, CA | Sonoma | North Coast, Region 1 | 57639 | n | 0-50 |  |  |  |  | $0-50 | $0 - $50
| y | 1 | MADRONE MUTUAL WATER COMPANY | Mutual |  | n | n |  | 0-25 | Monthly/ Annual Flat Rate | Unfamiliar; disinterested | [20 empty] | 1 | Cotati, CA | Sonoma | North Coast, Region 1 | 50667 | n | 50-100 |  |  |  |  | $0-50 | $0 - $50
|  | 1 | MAGIC MOUNTAIN MUTUAL WATER COMPANY | Mutual | P.O. Box 566 MONTE RIO, CA 95462 |  |  |  | 67 | [24 empty] | Sonoma | North Coast, Region 1 | 37308 | n | 100 | GW | Well | [8 empty] | A | 1. Total coliform MCL violation for March 2014 | 1. 5/8/14
y | y | 1 | MANILA COMMUNITY SERVICES DIST. | CSD | 1901 PARK ST. #3 ARCATA, CA 95521 | y | y | y | 357 | monthly/ annual flat rate; Sewer is flat rate. Water is flat rate plus $/hcf | Familiar; infrequent participation |  | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | Manila, CA | Humboldt | North Coast, Region 1 | 38816 | n | 1000 | GWP | CC - Humboldt Bay MWD Purchased |  |  | 75 | $51 - $100 |  | Manila’s water system is in good condition. The only major deficiencies associated with the existing system are some undersized water mains and inadequate storage capacity. The District has no major plans for system upgrades at this time. The Manila CSD is planning to carry out minor upgrades, such as replacing valves, installing new fire hydrants, and replacing the storage tank roof in the near future. The District is also applying for grants to increase water storage capacity. The District purchases its potable water from the Humboldt Bay Municipal Water District (HBMWD). Water is delivered to Manila by a 15-inch diameter main that continues south through Manila to serve the towns of Samoa and Fairhaven and the pulp mill. A 10-inch diameter main provides water to the District. The District provides water service for approximately 357 service connections (2003) consisting of 354 residential and 3 commercial/industrial. There is ample water from the supplier to meet future demands until maximum build-out of the District occurs. | Good condition | [7 empty] | sewer | The Manila CSD wastewater system is in good condition overall. The community relies on a Septic Tank Effluent Pump (STEP) system that pumps liquid effluent from septic tanks into a force main to the treatment facility. The treatment system consists of three free surface wetlands, two surface aerated facultative ponds, and four percolation ponds (rapid infiltration basins) for disposal. The system currently has approximately 444 connections, and flows currently range between 0.066 MGD during dry weather and 0.21 MGD during wet weather. The facility has an average dry weather flow design capacity of 0.14 MGD, and is operating at approximately 47% capacity. The District’s collection system and treatment system are in overall good condition. The system is in compliance with its waste discharge requirements and has sufficient capacity to serve forecasted potential future development without major improvements, although infrastructure extensions might be needed to serve a particular parcel. | Good condition
| y | 1 | MCCLOUD C.S.D. | CSD | P.O. Box 640, McCloud CA 96257/ 220 W Minnesota Street | y |  |  | 728 | [8 empty] | 1 | [14 empty] | McCloud, CA | Siskiyou | North Coast, Region 1 | 39083 | n | 1300 | GW | Springs (3), Intake Squaw Springs, Lower Elk Springs, Upper Elk Springs
| y | 1 | MARK WEST ACRES MWC | Mutual |  |  | n |  | 23 | Monthly/ Annual Flat Rate | Unfamiliar; disinterested | [21 empty] | Mark West Acres, Mark West Watershed | Sonoma | North Coast, Region 1 | 46037 | n | 0-50 |  |  |  |  | $0-50 | $0 - $50
| y | 1 | MARK WEST MUTUAL WATER CO. | Mutual |  | n | [26 empty] | Mark West Meadows, Sonoma County | Sonoma | North Coast, Region 1 | 46037 | n
y | y | 1 | MCKINLEYVILLE C.S.D. | CSD | P.O. BOX 2037 MCKINLEYVILLE, CA 95519 | y | y | y | 5616 | Increasing block (graduated) rate schedule | Familiar; infrequent participation | Unfunded | N/A | 1 | 0 | 1 | N/A | N/A | 0 | 0 | N/A | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | McKinleyville, CA: Pacific Ocean to the first eastern ridge and from Mad River north to Little River | Humboldt | North Coast, Region 1 | 46708 | n | 16900 | GWP | Purchase from Humboldt Bay MWD |  |  | 100-150 | $101 - $150 | purchased from HBMWD | The District’s current storage capacity for potable water is 5.25 million gallons in six storage tanks located on McCluski Hill (100,000 and 150,000 gallons), Cochran Road (1 million and 1.5 million gallons) and Norton Road (1 million and 1.5 million gallons). This can leave a 24-hour backup water supply for McKinleyville water customers at peak flow. Two new 3-million gallon tanks are also planned for construction on the District’s Murray Road site. McKinleyville CSD is in the process of determining the viability of the Murray Road tank site due to seismic considerations. A cost analysis will be conducted to determine the feasibility of design at that site opposed to purchase of a site in a less sensitive location. New tanks would increase the District's storage capacity, enhance fire flows during peak summer usage, and provide additional system capacity for new growth. McKinleyville CSD has determined it would be more advantageous to initiate phased construction of two tanks at this location to spread the cost over a longer period of time, and to enhance the operational flexibility of the system by having two tanks to allow for maintenance and redundancy. (McKinleyville CSD UWMP, Modified April, 2013.) Treated water is piped from the Essex Hill storage tank under the Mad River to the MCSD’s Grant A. Ramey Pump Station at the intersection of Azalea and North Bank Roads. The water is then boosted up to two storage tanks located at Cochran and Norton Roads and in-turn to a third higher elevation tank on McCluski Hill. This system provides a gravity-flow distribution of water to end users and fire hydrants throughout the water service area. A fourth undeveloped tank site on Murray Road has been purchased by the MCSD to serve future community water needs. The total potential system storage capacity is approximately six million gallons. The delivery system, from storage tanks to individual users, consists of about 70 miles of water mains. “McKinleyville and the City of Arcata’s water supply are vulnerable to natural disaster, therefore, an emergency intertie was constructed to allow for the flow of water to occur between both systems if necessary. This line remains stagnant when not in use, therefore, a 5/8-inch bypass was installed which allows the water within the intertie to turnover and maintain its chlorine residual. All water that passes through the bypass is metered and currently enters into the City of Arcata’s water system from the McKinleyville system.” (McKinleyville CSD UWMP, 2015: P 13) | Fair condition/ Upgrades planned/ identified |  |  |  |  | C | 1. NOV & Transmittal of the 3/13 Compliance Evaluation Inspection Report. Deficiencies include: laboratory deficiencies; not monitoring for pH and temperature daily; monitoring records not correlated with periods of discharge; O&M manual not being followed and in need of update. | 1. 4/23/13 | sewer | The McKinleyville CSD wastewater management facilities consist of two primary oxidation ponds (11.2 acres total), two secondary oxidation ponds (5.5 acres total), two finishing treatment marshes (5.6 acres total), with a total pond area of 22.3 acres. Biological treatment capacity of the ponds is 1.18 mgd (1,180,000 gallons per day) and hydraulic capacity of disinfection facilities (chlorine contact chamber) is estimated at 3.3 mgd (2300 gpm) peak flow. Treated wastewater is discharged to the Mad River during winter months when the river flow rate surpasses 200 cfs (cubic feet per second). During summer months (May 15 through September 30) and low flow periods of the Mad River, treated wastewater is discharged into two percolation ponds located adjacent to the river and is irrigated on dairy pastures in southwest McKinleyville. (McKinleyville CSD website, Wastewater Management Facility-About the Facility) The McKinleyville CSD completed a 20 Year Wastewater Facilities Plan (WFP) in January 2012, which identified a series of upgrades to the existing wastewater treatment plant, including portions of the effluent disposal system. Projected 20-year flows for year 2030 were developed based on a 1.8% annual increase in population. The projected average dry weather flow for year 2030 is 1.4 MGD and the projected average wet weather flow is 1.7 MGD. The projected peak day flow for year 2030 is 3.1 MGD. Based on the Wastewater Facilities Plan, the improvements will address the needs for the facility through the year 2030. The WFP presented several treatment alternatives and recommended replacing the existing facultative lagoon system with an in-basin extended aeration system. Subsequently, two manufacturers of in-basin extended aeration systems, Bioworks and Parkson, were chosen as the preferred vendors for the extended aeration system. The proposed Wastewater Management Facility (WWMF) improvements include a new headworks facility; aeration basins; a blower/electrical/maintenance building; two new secondary clarifiers, including return activated sludge/waste activated sludge pumping; and a biosolids storage basin. The improvement project was initiated in January 2016, and is currently under way. (McKinleyville CSD website, Wastewater Treatment Plant Upgrade, http://mckinleyvillecsd.com/wastewatermanagement-facility) | Fair condition/ Upgrades planned/ identified
y |  | 1 | MEADOW ESTATES MUTUAL | Mutual | 13250 ESTATE DRIVE BOONVILLE, CA 95415 PO Box 64, Boonville, CA 94515 | y | y | y | 35 | Increasing block (graduated) rate schedule | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | Meadow Estates Subdivision, Boonville, CA | Mendocino | North Coast, Region 1 | 36932 | n | 85 | GW | Wells (3) |  |  | 51-100 | $51 - $100 |  | The Company owns and maintains three active wells. | Adequate
|  | 1 | MELITA HEIGHTS MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
y | y | 1 | MENDOCINO CITY C.S.D. | CSD | P.O. Box 1030 (10500 Kelly Street) MENDOCINO, CA 95460 | y | y | y |  | uniform rate schedule; monthly/ annual flat rate | Unfamiliar; disinterested |  | 2 | 2 | 2 | 0 | 2 | 3 | 3 | 0 | 0 | 3 | 3 | 1 | 1 | 1 | 0 | 1 | 2 | 1 | 3 | 1 | Town of Mendocino, CA , Russian Gulch State Park and Headlands State Park | Mendocino | North Coast, Region 1 | 51277 | n | [5 empty] | 51-100 | $51 - $100 |  | We only have responsibility for ground water extraction. All members of the district obtain water from private wells or neighborhood private water companies. There is no central water distribution system in the district. Individual property owners receive their water from privately owned wells. The district has responsibility to monitor and control the amount of water extracted by each property owner. Groundwater is the primary water supply for the community of Mendocino; water trucked in during the summer months provides a secondary supply. Every developed parcel has a well; individual wells are used to supply both commercial and residential water use. In 1990, MCCSD adopted a Groundwater Management Plan (GMP) and Groundwater Extraction Permit Ordnance, 90-1. At the time of adoption two primary elements were included in the GMP: (1) groundwater extraction permitting procedures and; (2) mandatory water conservation requirements. Since adoption of the GMP the District has adopted additional programs to include: (1) a Voluntary Water Conservation Education Program; (2) a Groundwater Monitoring Program; (3) a Water Recycling Program; (4) a Data Management Program and; (5) a Water Shortage Contingency Plan. | Adequate | [7 empty] | sewer | The MCCSD Sewerage System is comprised of collection, treatment and disposal facilities. The District manages and maintains over 47,000 feet of collection system sewer lines and three lift stations. Since initial construction,the plant has been upgraded. In 1990 a belt filter press was added to de-water digested sludge to about 10%to 12% solids. In 2004, a dehydration unit was installed after the belt filter press to de-water sludge to Class A biosolids (greater than 90% solids and no pathogens). The Class A biosolids are transported to a sanitary landfill for final disposal.Treated effluent is discharged to a flow equalization pond which provides a constant discharge into the Pacific Ocean through a 996-foot outfall pipe. Since inception, the largest total annual flow through the system was in 2006. In that year, the total flow through the system was 45.55 million gallons; all but two million gallons weredischarged to the ocean. In 1997, the District installed a recycled water system that pumps treated effluent to the Mendocino High School to irrigate the athletic fields. This system provides about two million gallons of water per year to the High School. The District’s collection system overlies the community’s shallow unconfined aquifer. Groundwater is the primary water supply for the Mendocino community. Individual wells are used to supply both commercial and residential water use.Many of these wells are near the wastewater collection systempipes. Because of thi scircumstance, the District is very concerned about any overflows from the system and potential exfiltration to the aquifer. The District has developed a proactive operation and preventive maintenance program known as the Collection System Operation and Maintenance Program (CSOMP). (See below for additional information on this program) Based on the District’s efforts with this program, it appearsthat most of the additional flow to the plant during wet years or the wet time of the year is caused by additional water consumption and/or is caused by inflow rather than infiltration. Inflow can occur through manholes, gutter drops from houses,yard drains, lateral cleanouts orother similar kinds of connection issues on individual parcels.The district also indicates that much of the additional flow is from the unlined emergency overflow pond and drying beds. The District has also observed that much of the increased flow happens immediately after a rain event which indicates inflow rather than infiltration. | Fair condition/ Upgrades planned/ identified
|  | 1 | MENDOCINO COUNTY WATER WORKS DISTRICT NO. II | County Dist | [29 empty] | Mendocino | North Coast, Region 1 | 40185 | n
|  | 1 | MICHELE MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 42958 | n | 170 | GW | Wells (2)
|  | 1 | MILL CREEK M.W.C. | Mutual | P O BOX 864 FORTUNA, CA 95540 |  |  |  | 36 | [24 empty] | Humboldt | North Coast, Region 1 | 49403 | n | 65 | GW | Wells (2)
|  | 1 | MILLVIEW COUNTY WATER DISTRICT | Water Dist | 3081 NORTH STATE STREET UKIAH, CA 95482 | y |  |  | 1608 | graduated block - in addition to a meter charge, the MCWD charges a fee of $3.42 for every 1,000 gallons, which goes to O&M and capital improvements (implemented 2009) | Unfamiliar; interested | [21 empty] | Millview, CA; The MCWD serves an 8.5-square-mile service area northeast and immediately north of Ukiah city limits. | Mendocino | North Coast, Region 1 | 19356 | p | 5568 | SW | Russian River Intake, Instream, Wells (3), Wells, Surface influenced (16) |  |  |  |  | The plant consists of three river intake pumps, four horizontal press filters, two clearwells, and three high-service pumps. The plant is normally used in the summer months, due to higher demands. | The MCWD receives most of its water from surface water rights. In addition, it can purchase up to 1,520 acre-feet (AF ) of Lake Mendocino water. During the period from 2000 to 2009, the MCWD was able to meet demand. The average demand from 2000 to 2008 was 1,462 AF and production was 1,556 AF. Demand for a year with normal precipitation (2004) was 1,522 AF, which is used as the baseline for projections to 2030.The MCWD has sufficient supply to serve its customers through 2015. A recent cease and desist order would reduce available supply by 785 acre-feet per year (AFY). The order is being contested; however, if it is upheld, the MCWD would have difficulty supplying water in 2020 and beyond unless it can purchase additional Lake Mendocino water or find another source. The MCWD also owns and operates a treatment plant capable of treating 2400 gallons per minute. The plant is located at 2850 Redemeyer Road (Exhibit 3.2-1 ). It has a design capacity of 3.0 million gallons per day (mgd). Average daily demand is 1.7 mgd, maximum daily demand is 2.7 mgd. The plant has sufficient capacity to meet an estimated peak demand of 2.8 mgd. The plant consists of three river intake pumps, four horizontal press filters, two clearwells, and three high-service pumps. The plant is normally used in the summer months, due to higher demands. The MCWD also owns and operates a well field located immediately adjacent to the existing water treatment plant. The well field is used to provide water through the water treatment plant and to the distribution system for a majority of the year. During the summer higher demand period, groundwater is blended with treated surface water.The MCWD has a storage capacity of 3.24 million gallons or approximately two days’ supply. The MCWD also maintains two pump stations located in the Deerwood subdivision that pump water to and from its storage facilities. The MCWD’s existing infrastructure is sufficient to meet current demand; as additional supplies are secured, the MCWD can increase treatment plant capacity and storage to meet demands of additional new services. However, with the moratorium, expansion is not contemplated in the near future. The MCWD offices have moved to 151 Laws Avenue, which houses the RRFC and WCWD, and shares office space with the staff of the Willow County Water District. This move has resulted in the cross training of office staff, field personnel and the opportunity to combine resources, reduce cost, and provide more efficient service to better serve the customers of the districts. The MCWD occasionally uses the boardroom at that location for special meetings.City of Ukiah to the south and the CCWD to the north. In addition, the MCWD treats and wheels water to CCWD. The MCWD also has a contract to purchase Lake Mendocino Water from the RRFC. | Uncertain water supply
y | y | 1 | MIRANDA C.S.D. | CSD | P.O. BOX 160 MIRANDA, CA 95553 | y | y | y | 142 | uniform rate schedule | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 0 | Miranda, CA within the District boundaries | Humboldt | North Coast, Region 1 | 33438 | n | 600 | GW | Wells (2) |  |  | 0-50; Sewer - $23 monthly, water $12.00 monthly for basic - extra charges for more than 1200 cubic feet. The District is in the process of determining how much to raise the rates, which should be completed this year. | $0 - $50 | The pumps are operated in a lead lag arrangement, with the larger pump leading during summer months and the smaller pump leading during winter months. There are 6-inch asbestos cement (AC) and ductile iron pipes from the wells to the treatment building. Continuous disinfection is provided through a BIF metering pump that injects calcium hypochlorite into the main line. The meter is switched on by the well pumps. Soda ash is used to raise the pH of the water, which is typically around 6.1. | The District’s water source is two wells with a total capacity of 0.338 MGD. The District has 0.2 MG of total storage, and the distribution system consists of one pressure zone which is gravity fed by the two tanks. Low pressures are known to occur, especially in the School Road area, due to small diameter (2-in.) mains. Miranda’s water system is in fair to good condition. The primary deficiencies associated with the existing system are some undersized water mains and inadequate storage capacity. The District has 0.2 MG of total storage in the form of two 100,000 gallon tanks, one redwood and one bolted steel. The redwood tank was installed in 1964, and the bolted steel tank was installed in 1978. Both tanks are in good condition. The distribution system consists of one pressure zone, which is gravity fed by the two tanks. Low pressures are known to occur, especially in the School Road area, due to small diameter (2”) mains. This problem is exacerbated when fire hydrants are in use. The District has 20 fire hydrants. | Fair condition/ Upgrades planned/ identified | The system has had some action level exceedances for copper and lead in the past, but these issues seem to have been resolved by the addition of soda ash feed. | [6 empty] | septic - centralized collection | The Miranda CSD collection system consists of small diameter gravity sewer lines that collect effluent from individual septic tanks in the community. The system is a combined septic tank effluent gravity and pump system (STEG/STEP). The treatment plant has a dry weather design capacity of 46,000 gpd, as set forth in their waste discharge requirements. The Miranda CSD uses percolation ponds for disposal. This form of disposal is becoming increasingly difficult to permit due to stringent regulations governing disposal to the South Fork Eel River during the discharge prohibition period from May 15th through September 30th. This discharge prohibition period extends to all wastewater dischargers on Eel River as covered by the Water Quality Control Plan for the North Coast Region. | Regulatory - septic
y |  | 1 | MOBILE HOME ESTATES | Other | 5761 Old Redwood Highway North SANTA ROSA, CA 95403 | n - contract with Willow CWD | y | y | 148 | water is included with rent | Unfamiliar; disinterested |  | 1 | 1 | 2 | 2 | 2 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 2 | 1 | 5761 Old Redwood Highway | Sonoma | North Coast, Region 1 | 46037 | n | 320 | GW | well |  |  | 0-50 | $0 - $50 | No treatment but manganese levels are high and problematic in system | No treatment but manganese levels are high and problematic in system | Fair condition/ Upgrades planned/ identified |  | F | 1. Failure to submit 2014 Annual report to the Division 2. Total coliform monitoring and reporting violation for June 2015 3. Failure to comply with treatment technique 4. Treatment technique violation for July 2015 5. Citation for the source flow meter 6. Monitoring and reporting violation for November 2012 | 1. 7/17/15 2. 7/24/15 3. 7/29/15 4. 8/25/15 5. 7/25/17 6. 1/8/13 |  |  |  | sewer
|  | 1 | MONTAGUE, CITY OF | City | P.O. BOX 428 MONTAGUE, CA 96064 |  |  |  | 503 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Siskiyou | North Coast, Region 1 | 40938 | n | 1495 | SW | Lake Shastina - raw, Little Shasta River - raw | [8 empty] | C | 1. Violation of MCL for total Trihalomehtanes (TTHM) in drinking water | 1. 3/19/13
| y | 1 | MONTAGUE WATER CONSERVATION DISTRICT | Water Conservation Dist |  | n | y |  | 50-100 | Uniform Rate Schedule | Familiar; infrequent participation | Funded | [18 empty] | 1 | 1 | Montague, Siskiyou County | Siskiyou | North Coast, Region 1 | 40938 | n | 1,000-5,000 |  |  |  |  | $49 per acre/foot; Over $100 | $101 - $150
y |  | 1 | Montair Subdivision Homeowners Association | Wastewater | Highway 3 & Montague Road, Montague, CA 96064 | y | n | don't know | 0-50 | monthly/ annual flat rate |  |  | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Montair Estates, near Montague, CA | Siskiyou | North Coast, Region 1 | 54844 | n |  |  |  | each household |  | Each home is charged a fee of approximately $150 per quarter. This fee goes into many HOA services, including the wastewater treatment facility. | $0 - $50 | [10 empty] | sewer
|  | 1 | MOONSTONE HEIGHTS MWA | Mutual | P.O. Box 854 TRINIDAD, CA 95570 |  |  |  | 14 | [24 empty] | Humboldt | North Coast, Region 1 | 50417 | n | 31 | GW | well | [8 empty] | 0 | 1. Failure to conduct or report monthly coliform sampling | 1. 8/14/14
|  | 1 | MOUNT WESKE ESTATES MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 39614 | n
|  | 1 | MOUNTAIN VIEW MOBILE ESTATES, LLC | Other | 2860 Santa Rosa Ave Santa Rosa, CA 95407 |  |  |  | 111 | [24 empty] | Sonoma | North Coast, Region 1 | 44604 | n | 250 | GW | Wells (2)
y | y | 1 | MYERS FLAT M.W.S. INC. | Mutual | P.O. BOX 74 MYERS FLAT, CA 95554 | y | n | y | 102 | Increasing block (graduated) rate schedule | Familiar; infrequent participation |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | Myers Flat, CA | Humboldt | North Coast, Region 1 | 33438 | n | 400 | GW | Wells (2) |  |  | 51-100; There is a base rate of $57.00 and a $8.00 surcharge which equals $65.00 total, excluding excess use charges. We also have an $8 surcharge for the CIP. | $51 - $100 |  | In the last 5 years we have started replacing the old lines with new and by 2020 hope to have all new lines and meters in place. | Fair condition/ Upgrades planned/ identified |  | 0 | 1. Failure to conduct or report monthly coliform sampling | 1. 10/14/14 | [7 empty] | 1
|  | 1 | NEVES FAMILY TRUST WATER SYSTEM | Other | [29 empty] | Sonoma | North Coast, Region 1 | 90179 | n
|  | 1 | NEWELL COUNTY WATER DISTRICT | Water Dist | 405 5TH ST. TULELAKE, CA 96134 |  |  |  | 210 |  | Familiar; infrequent participation | Funded | [21 empty] | Modoc | North Coast, Region 1 | 33909 | n | 300 | GW | Wells (3)
|  | 1 | NOEL HEIGHTS-CAL WATER SERVICE (PUC) | Public Utility | 1720 NORTH FIRST STREET SAN JOSE, CA 95112 |  |  |  | 49 | [24 empty] | Sonoma | North Coast, Region 1 | 40469 | n | 137 | GU | Well
y |  | 1 | NORTH GUALALA WATER COMPANY | Public Utility | 38958 Cypress Way P.O. Box 1000 GUALALA, CA 95445 | y | y | y | 1052 | CPUC authorized rate structure based on expected expenses and revenues. Useage based with two tiers and fixed charges in combination. | Familiar; lack resources to participate |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 0 | 1 | 1 | 0 | 3 | 2 | Gualala, CA, Anchor Bay, and surrounding areas | Mendocino | North Coast, Region 1 | 40185 | n | 2630 | SW | Instream - Big Gulch, Instream - Robinson Gulch, Wells (2 + 3 pending) |  |  | 51-100 | $51 - $100 |  |  |  | Occasional issues with non maintained leach fields in sources watersheds
|  | 1 | NORTH STAR MOBILE HOME PARK | Other | 3200 Santa Rosa Avenue SANTA ROSA, CA 95407 |  |  |  | 76 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 75 | GW | Well | [8 empty] | 0 | 1. Nitrate monitoring and reporting violation for first quarter 2013 | 1. 6/10/13
|  | 1 | NOYO HARBOR DISTRICT | Harbor Dist | [29 empty] | Mendocino | North Coast, Region 1 | 31027 | n | [14 empty] | D | 1.Notice of Violation of 9/9/15 Water Quality Certification and Regional Water Board Order No. 86-51 | 1. 4/15/2016 2. 12/7/16
|  | 1 | OAK VALLEY ACRES P.O.A. | Other | P O BOX 86 YREKA, CA 96097 |  |  |  | 26 | [24 empty] | Siskiyou | North Coast, Region 1 | 25493 | n | 80 | GW | Well
|  | 1 | OCCIDENTAL COMMUNITY SERVICES DISTRICT | CSD | [29 empty] | Sonoma | North Coast, Region 1 | 69219 | n
|  | 1 | OCCIDENTAL COUNTY SANITATION DISTRICT | Sanitary Dist | [6 empty] | Familiar; infrequent participation | Unfunded | [21 empty] | Sonoma | North Coast, Region 1 | 69219 | n | [15 empty] | 1. Admin Civil Liability 2. Cease and Desist Order | 1. 9.5.2019 2. 12.06.2012
y |  | 1 | Odd Fellows Recreation Club | other | 9090 Gilroy Avenue, Guerneville, CA 95446 | y | y | y | 259 |  | Unfamiliar; lack resources to investigate/participate |  | 0 |  | 1 | 1 | N/A | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | The Odd Fellows Recreation Club in Guerneville | Sonoma | North Coast, Region 1 | 40469 | n | 80 | GW | Wells (3) | [14 empty] | sewer
| y | 1 | ORICK C.S.D. | CSD | P.O. BOX 224 ORICK, CA 95555 | n | y |  | 140 | Increasing Block (Graduated) Rate Schedule | Familiar; infrequent participation | Funded | [5 empty] | 1 |  |  |  | 1 | 1 |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | Orick, CA | Humboldt | North Coast, Region 1 | 47621 | n | 450 | GW | Wells (2) |  |  | 0-50 | $0 - $50 |  | The initial system construction of the water system served most of the residents of the Orick Community. The original system (1977-1978) consisted of two 60 foot wells with 10 hp submersible pumps, a 100,000 gallon redwood storage tank, and 8-inch, 6-inch, and 4-inch distribution lines. In 1978, an 8-inch line was extended southwest along the north side of Route. 101 in anticipation of the 1987 expansion. The 8-inch line was extended west past Hilton Road to the National Park Service Visitors’ Center in 1987. The pumping capacity of the District’s water system is approximately 288,000 gallons per day. The system demand is approximately 216,000 gallons per day. The system demand is approximately 75% of the system pumping capacity. Currently 139 of 142 service connections provided by the water facility are being served. The District maintains two active wells with a total production capacity of 0.274 MGD. The District maintains one pressure zone in its distribution system, serviced by approximately 6 miles of 4-inch through 8-inch PVC and AC pipe. The District’s storage capacity includes two 100,000 gallon redwood storage tanks. This represents less than one day of needed storage. Water service within Orick is generally good. A significant deficiency of the current water system is its lack of proper storage, which is less than one day at maximum day demands. | Storage capacity insufficient | [7 empty] | septic - centralized collection | Pollution from failing septic tanks has been found to be widespread and contaminating local groundwater sources. The Orick CSD applied to the Humboldt LAFCo to activate their latent powers to provide community wastewater services, with wastewater service to be limited to the commercial/residential areas of the Orick community along Hwy 101 on the north and south sides of Redwood Creek. LAFCo took action to authorize this additional power in May 2011. The Orick CSD recently evaluated alternatives for a community wastewater system and completed an EIR (State Clearing House No. 2009082034) evaluating a Septic Tank Effluent Pump system where effluent would be pumped through collection piping to an advanced treatment system and then disinfected and discharged to subsurface disposal field(s). The system was intended to have a design buildout to serve 371 equivalent residential units, and flows are expected to range between an average dry weather flow of 43,041 gpd to a peak day average flow of 86,081 gpd (Draft Environmental Impact Report Orick Wastewater Project Orick CSD, October 2011). Following this effort, the Orick CSD received funding from the North Coast Resource Partnership to conduct a demonstration project to evaluate the feasibility of a decentralized community wastewater system. The Orick CSD will need ultimately to identify a preferred wastewater system, design and feasible project, and seek regulatory approval and adequate funding. In the meantime, owners wishing to develop their land may do so using onsite sewage disposal systems. Site conditions may require that non-standard systems be used, such as Wisconsin Mounds or At-Grade systems that do not use subsurface leach lines for effluent disposal, which may require inspection and monitoring. | Fair condition/ Upgrades planned/ identified
y | y | 1 | ORLEANS C.S.D. | CSD | P.O. Box 303 ORLEANS, CA 95556 | y | y | n | 139 | Increasing block (graduated) rate schedule | Unfamiliar; interested |  | 0 | 1 | 3 | 0 | 3 | 3 | 0 | 1 | 0 | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | Orleans, CA | Humboldt | North Coast, Region 1 | 40129 | n | 630 | SW | IN- Pearch Creek - raw |  |  | 0-50 | $0 - $50 | Water flows by gravity to treatment, where it is prechlorinated and then filtered through three parallel Permutit automatic backwash filters. | Orleans CSD water supply consists of an infiltration gallery within Pearch Creek with unknown but adequate capacity. Orleans CSD currently uses inline filtration, which is no longer an accepted filtration technology in the State of California. As a result, the District has recently applied to fund a project which includes a fourth filter, turbidity meters, a second 100,000 gallon storage tank, and a new exit flow meter to replace the high flow turbine meter. Additionally, it has been proposed by the District to move the polymer and chlorine injection point further uphill from the current treatment point, which could provide the necessary flocculation time to change the system from inline to direct filtration (NCRP Demonstration Project for Orleans Community Services District, January 2015). The Orleans CSD received funding from the North Coast Resource Partnership to conduct a demonstration project to evaluate water demand, water storage, water rights, a water shortage plan, and develop strategies for addressing those needs. OCSD’s water supply consists of an infiltration gallery within Pearch Creek with unknown but adequate capacity. Water flows by gravity to treatment, where it is prechlorinated and then filtered through three parallel Permutit automatic backwash filters. The District recently began feeding polymer or other coagulant. Water is then stored in a 100,000 gallon redwood tank and fed to distribution. Two pressure zones exist within the system, with one zone served by the redwood storage tank and a second zone served by a booster pump. The distribution system consists of mostly asbestos cement pipe with some ductile iron, PVC, and steel, all ranging in size between 2 inches and 8 inches in diameter. The distribution system was installed in 1977 and 1997. | Fair condition/ Upgrades planned/ identified
|  | 1 | ORLEANS MUTUAL WATER CO. | Mutual | P O BOX 54 ORLEANS, CA 95556 |  |  |  | 38 | [24 empty] | Humboldt | North Coast, Region 1 | 40129 | n | 85 | SW | IN - Crawford Creek -raw |  |  |  |  | Orleans CSD currently uses inline filtration, which is no longer an accepted filtration technology in the State of California. As a result, the District has recently applied to fund a project which includes a fourth filter, turbidity meters, a second 100,000 gallon storage tank, and a new exit flow meter to replace the high flow turbine meter. Additionally, it has been proposed by the District to move the polymer and chlorine injection point further uphill from the current treatment point, which could provide the necessary flocculation time to change the system from inline to direct filtration (NCRP Demonstration Project for Orleans Community Services District, January 2015). The Orleans CSD received funding from the North Coast Resource Partnership to conduct a demonstration project to evaluate water demand, water storage, water rights, a water shortage plan, and develop strategies for addressing those needs. Orleans CSD water supply consists of an infiltration gallery within Pearch Creek with unknown but adequate capacity. |  |  |  | B | 1. Failure to comply with combined filter effluent turbidity performance standards 2. Failure to comply with combined filter effluent turbidity performance standards | 1. 6/15/2016 2. 10/21/14
|  | 1 | PACIFIC REEFS WATER DISTRICT | Water Dist | P.O. Box 314, Albion, CA 95410 | n |  |  | 17 of 24 lots | tiered to encourage water conservation | Familiar; infrequent participation | Funded | [20 empty] | Pacific Reefs, a small 25-lot sudivision | Mendocino | North Coast, Region 1 | 39667 | n | 48 | [6 empty] | All water flows through a chlorinator before being pumped into the District’s two storage tanks. | The District’s water supply consists of two springs and a well, both of which are located within the subdivision and District boundaries, and on District-owned land. The well is equipped with a pump that operates at approximately 1.5 gallons per minute (gpm). The spring water is also collected and pumped to the storage tanks. All water flows through a chlorinator before being pumped into the District’s two storage tanks. The storage tanks include a 40,000 gallon steel tank (which collapsed in May 2013) and a 20,000 gallon wooden tank. The District is planning to replace the 40,000 gallon tank. The existing storage is estimated to be the equivalent of 57 days of average usage. A number of lot owners have private wells; however, the District has infrastructure in place and provides backup water service in the event of well failure. The District owns the small parcel on which the spring/well and water storage tanks are located, as well as the two water tanks and pumphouse facilities. The storage tanks include a 40,000 gallon steel water tank (now collapsed and to be replaced), a 20,000 gallon wooden tank, both built in 1960 and renovated in 2005. The useful life of the water system is estimated at 15-30 years. | Good condition
|  | 1 | PALMER CREEK CSD | CSD | P.O. Box 309 FORTUNA, CA 95540 |  |  |  | 131 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Humboldt | North Coast, Region 1 | 49403 | n | 320 | GW | Well |  |  |  |  | Water pumped from the wells is injected with chlorine and then sent to a contact basin prior to filtration through a Loprest package treatment plant designed to remove iron and manganese from the groundwater. The plant consists of a reaction vessel and three pressure filters, after which water is boosted to storage and distribution. | Palmer Creek CSD’s water supply consists of two active wells, each capable of pumping 80 gpm. The District has one 200,000 gallon storage tank that serves two pressure zones; one has reduced pressures through a PRV. The distribution system consists of approximately 38 miles of PVC, cast-iron and asbestos cement pipe ranging in size from 2 inches to 10 inches. Palmer Creek CSD produced more than 11 million gallons of drinking water in 2003. Average daily use is estimated at approximately 0.031 MGD, and peak daily use is estimated at approximately 0.084 MGD. The District has approximately 150 service connections, of which 127 are active connections. All active connections are metered. The Palmer Creek CSD water distribution system was constructed in 1997. Palmer Creek CSD produced more than 11 million gallons of drinking water in 2003. Average daily use is estimated at approximately 0.031 MGD, and peak daily use is reported at approximately 0.084 MGD. The District has approximately 128 metered water service connections. The water system was designed to serve 187 residential connections. Based on present and projected water use levels, Palmer Creek CSD has the ability to meet the water demands of development of the remaining lots in the District without the need to supplement supplies or storage and delivery systems. (Humboldt LAFCo - Palmer Creek CSD Municipal Service Review, 2007) | Good condition | [7 empty] | sewer | The Palmer Creek CSD collects wastewater from service connections within its District and conveys it to a metered interconnection point with the City of Fortuna wastewater system for treatment and disposal, pursuant to a contract for service. There are 154 existing residential wastewater connections within the Palmer Creek CSD generating an average dry weather flow of 20,000 gpd (gallons per day) and wet weather flows of 30,000 gpd (Humboldt LAFCo - Palmer Creek CSD Municipal Service Review, 2007). The Palmer Creek CSD reports that it is currently at its contracted limit for wastewater flows. The contract with the City would need to be amended to allow additional development within the District. Discussions regarding the wastewater agreement between the City and the District are ongoing. | Adequate
y |  | 1 | PALOMINO ESTATES M.W.C. | Mutual | 111 PALOMINO WAY GARBERVILLE, CA 95542 | y | y | n | 19 | Monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 2 | 0 | Palomino Estates on East Branch Rd. in Benbow Ca., Garberville is all Benbow residents mailing address. | Humboldt | North Coast, Region 1 | 36371 | n | 64 | SW | IN - Eel River infiltration gallery - raw |  |  | 100-150 | $101 - $150 | triple media filter for arsenic |  |  |  | A | MCL Total coliform violation June 2017, Total coliform monitoring violation for April 2017, monitoring and reporting violation for June 2017 | 7/25, 2017 |  |  |  | septic | each home has own septic | Adequate |  | 1
|  | 1 | PALOMINO LAKES MUTUAL WATER CO. | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 37411 | n
|  | 1 | PARK ROYAL MUTUAL WATER | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
|  | 1 | PATRICK CREEK COMMUNITY SERVICE DISTRICT | CSD | 5045 Patrick Creek Drive Mckinleyville, CA 95519, 707.839.2355 | [28 empty] | Humboldt | North Coast, Region 1 | 46708 | n | 70 | [7 empty] | The District originally had its own water system. However, in 1973, the Patrick Creek Community Services District (PCCSD) transferred interest in the distribution system to the McKinleyville Community Services District where water obtained from the HBMWD is distributed. The water system currently serves 17 homes, with a total capacity of 18 homes. One household has two lots, and the rest are single lots. With the exception of the possibility of the double lot ownership, the district is at capacity. | Adequate
| y | 1 | PHILLIPSVILLE C.S.D. | CSD | P.O. BOX 231 PHILLIPSVILLE, CA 95559 | n | y |  | 66 | Increasing Block (Graduated) Rate Schedule | Unfamiliar; interested | [8 empty] | 1 | [12 empty] | Phillipsville, CA | Humboldt | North Coast, Region 1 | 33438 | n | 300 | SW | Spring - raw, Well |  |  | $0-50 | $0 - $50 | The well is continuously disinfected with a chlorination feed system located in the well housing. | PCSD’s water supply consists of a groundwater well of unknown capacity and a surface water spring source with variable capacity. The spring source is unable to meet summertime demands, and therefore only serves the upper portion of the system during low flows while the well supplies water to the rest of the system. The well is primarily used during dry months. The spring is believed to be under the influence of surface water, is not filtered, and is continuously chlorinated. The system has a total of eight storage tanks ranging in size from 250 gallons to 60,000 gallons for a total combined capacity of 74,850 gallons. The system has numerous small pressure zones with anywhere between two and four connections. The distribution system consists of a variety of piping, not all of which meet standards. The exact amounts of any particular piping are unknown. Some electrical conduit is currently being used for water piping. The system has replaced approximately 2,050 feet of piping since 2000 with PVC piping. According to the 2004 DHS annual inspection report, PCSD retailed an estimated 8.75 million gallons of drinking water in 2003. Average daily use for the entire District is estimated at 0.024 mgd, and peak daily use is estimated at approximately 0.085 mgd. The Phillipsville area has approximately 65 active service connections. The system does not have a master meter to monitor production. The Phillipsville CSD water system was in poor condition with inadequate storage capacity, a distribution system consisting of non-standard materials such as electrical conduit, limited source capacity, and lack of treatment. The District received American Recovery and Restoration Act funding through DDW and upgraded the water system infrastructure to resolve these issues. The project included the installation of a treatment plant on the spring source, the replacement of distribution pipes, and the installation of a 140,000 gallon storage tank. The project was completed in 2012. The improvements were designed to serve existing development plus ten percent additional capacity to accommodate some growth. The state DDW reports issues with the system remain relating to the turbidity of water that feeds a spring that serves the upper portion of the District and the need for additional storage. The drinking water system is adequate for current needs and does not have significant deficiencies (2014 Housing Element Attachment J, Detail of Infrastructure and Service Needs of Legacy Communities). | Fair condition/ Upgrades planned/ identified | The well has high levels of iron and manganese and suffers from low pH, which causes problems with coloration and corrosion of the distribution system.
|  | 1 | Pine Cove RV Park | Trailer Park | 9435 TRINITY DAM BLVD. #5 LEWISTON,CA 96052 |  |  |  | 68 | [24 empty] | Trinity | North Coast, Region 1 | 39583 | n | 255 | GW | Wells (2)
y |  | 1 | PINE GROVE Mobile Home PARK | other | 2100 NORTHCREST DRIVE CRESCENT CITY, CA 95531 | n - contract with Willow CWD | y | y | 51 | included with rent | Unfamiliar; disinterested |  | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 |  | 1 | 1950 Northcrest Dr. & 2200 Northcrest Dr. Crescent City Ca. | Del Norte | North Coast, Region 1 | 26544 | n | 100 | GW | well | [7 empty] | Chromium6 exceedence. | [6 empty] | sewer
|  | 1 | PINE HILL TERRACE MOBILE HOME PARK | other | 3195 Gravenstein Hwy North SEBASTOPOL, CA 95472 |  |  |  | 23 | [24 empty] | Sonoma | North Coast, Region 1 | 99141 | n | 27 | GW | Well
y |  | 1 | PINE MOUNTAIN MUTUAL WATER CO. | Mutual | 4551 Ridgewood Road WILLLITS, CA 95490 | y | y | n | 124 | Monthly/ annual flat rate | Unfamiliar; interested |  | 1 | 3 | 1 | 0 | 2 | 2 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 3 | 0 | 0 | 2 | 1 | 3 | 2 | Pine Mountain Estates, Willits, CA | Mendocino | North Coast, Region 1 | 32667 | n | 310 | SW | IN - Chinquapin Lake intake - raw |  |  | 61 - 80 | $51 - $100 |  | The Company owns and maintains three active wells, the Chinquapin Lake Intake, approximately six miles of pipeline, and a pump station. | Adequate | The Safe Drinking Water Information System lists the more recent monitoring violation dated 2013 with compliance achieved June 3, 2013. The USEPA notesone monitoring and reporting violation on record dated March 31, 2013,with compliance achieved July 6, 2016 for this water system. | C | 1. Failure to sample for disinfection byproducts 2. Compliance order for violation of section 116555 of the California Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 6/3/13 2. 10/17/14 | [7 empty] | 1
|  | 1 | PLAZA MOBILE HOME PARK | other | 871 38TH AVENUE SANTA CRUZ, CA 95062 |  |  |  | 71 | [24 empty] | Sonoma | North Coast, Region 1 | 29250 | n | 125 | GW | Well (2)
|  | 1 | POINT ARENA WATER WORKS | private water company | P.O. BOX 205 POINT ARENA, CA 95468 135 Hay Parkway, Pt Arena, CA 95468 |  |  |  | 194 | [23 empty] | City of Point Arena | Mendocino | North Coast, Region 1 | 40208 | n | 646 | GW | Well (2) | [5 empty] | The Garcia River is the primary water supply for the company, which withdraws water from one 24-inch diameter well and one 12-inch well. Three secondary wells at Whiskey Shoals are also utilized. An average of 12,370 CCF (hundreds of cubic feet) are pumped each year, which is equivalent to 9.2 million gallons or 28.4 acre feet per year. Average water usage is 87 gallons per residential customer per day, which is very low and indicates water conservation measures are in place. Company storage facilities include a 285,000 gallon concrete tank and a 272,000 wooden tank. The water distribution system is via approximately 46,000 lineal feet of pipe, primarily 6-inch, 8-inch and 12-inch, although some 2-inch and 4-inch lines are still in use. Although the company’s infrastructure is in relatively good shape, water storage and insufficient fire-flow problems were identified in a 2004 report, the “Water System Master Plan and Feasibility Analysis.” Water storage for firefighting is addressed above. Limitations on fire flow water occur in Zone 1 (the downtown area), which has existing 6-inch water lines. These lines will not be replaced until there are sufficient funds to do so. (William Hay, PAWW; personal communication). PAWW has a current application pending before the CPUC to renew its permit for up to 100 acre-feet of water per year; and a second application to add another 50 acre-feet to the allocation. | Storage capacity insufficient
|  | 1 | Point Arena WWTP | Sanitary Dist | Iverson Road, Point Arena, CA 95468 |  |  |  | 364 | [24 empty] | Mendocino | North Coast, Region 1 | 40208 | n | 450 | [17 empty] | The City operates and maintains a Wastewater Reclamation Facility (treatment plant); approximately 11,000 lineal feet of 6-inch diameter sewage collection mains; one pump (lift) station; and four 17,000 square foot percolation ponds. The treatment plant is located at the intersection of Iverson Avenue and Port Road adjacent to Arena Creek. The lift station is located at the Arena Cove parking area. The percolation ponds are located on top of the south bluff off Bluff Top Road.The treatment facility is designed to provide secondary treatment for up to 0.13 million gallons of wastewater per day (mgd), average dry weather flow. Treatment consists of two aerated ponds which operate in series, followed by disinfection prior to being discharged to the percolation ponds. Pumps are utilized to transport the chlorinated effluent via an 8-inch force main 3,400 feet to the ponds. The ponds have sufficient capacity during most of the year. However, during large wet weather conditions, the ponds are not able to keep up with the effluent flows so a 20 -acre pasture is utilized for treated effluent spray irrigation. The pasture is located on the bluff adjacent to the percolation ponds.The wastewater system operates under waste discharge requirements of the North Coast Region, California Regional Water Quality Control Board including Monitoring and Reporting Program No. R1-2003-001. The treatment plant currently treats an average of 0.0383 mgd, dry weather flow; and 0.0797 mgd, wet weather flow. Improvement recommendations were made in a 2006 sewer system analysis by Coastland Engineering, and include replacing specific line segments, repairing laterals and manholes to reduce inflow and infiltration (I&I), and improvements to the treatment ponds. A more recent engineering study by Winzler & Kelley in 2010 addressed sludge removal and I&I. | Fair condition/ Upgrades planned/ identified
| y | 1 | Point Arena Lighthouse Keepers | other |  |  |  |  | 4 | [22 empty] | 1 | Point Arena Lightstation, Mendocino County | Mendocino | North Coast, Region 1 | 40208 | n | 60
y |  | 1 | POINT CABRILLO HIGHLANDS | other | PO Box 20575, Oakland, CA 94620 | n | y | don't know | 21 | Monthly/ annual flat rate; included in rent | Unfamiliar; lack resources to investigate/participate |  | 0 | 1 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | small trailer park and cottages at Point Cabrillo Highlands | Mendocino | North Coast, Region 1 | 56250 | n | 42 | GW | Well | [5 empty] | Bottom line is he's a sole proprietor, doesn't make much money off of it, but would like funding to redo it. Been toying with an idea of creating a big pond - another well put in to fill it, possible use for fire suppression. | Adequate
y | y | 1 | POINT OF VIEW MUTUAL WATER CO | Mutual | P.O. BOX 841 MENDOCINO, CA 95460 | n | y | y | 28 | monthly/ annual flat rate; Annual assessments set by Board one year in advance; special assessments on top IF needed (Only one in past 18 years); Misc. income from excessive water use penalties (5 cents per gallon for every gallon over avg. 200 gpd based on monthly meter readings; no exceptions) | Familiar; not a participant |  | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 32 lot subdivision on Palette Drive, unincorporated town of Mendocino, CA | Mendocino | North Coast, Region 1 | 51277 | n | 57 | GW | Wells (4) |  |  | 51-100 | $51 - $100 |  | The Company owns and maintains four active wells and approximately one mile of pipeline. In addition, the Company own sa storage tank, pumping, and treatment facilities. | Adequate | Only low pH which we use NaOH treatment for
|  | 1 | RAINS CREEK WATER DISTRICT | Water Dist | P.O. BOX 956 FORESTVILLE, CA 95436 |  |  |  | 64 | [24 empty] | Sonoma | North Coast, Region 1 | 49732 | n | 180 | GW | Well | [8 empty] | C | 1. Compliance order for violation of section 116555 of CA Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 10/17/2014
|  | 1 | RANCHO DEL PARADISO-CAL WATER SVC (PUC) | Public Utility | 1720 NORTH FIRST STREET SAN JOSE, CA 95112 |  |  |  | 57 | [24 empty] | Sonoma | North Coast, Region 1 | 58333 | n | 162 | GWP | CC - Purchased from Sweetwater Springs CWD - Monte Rio; Instream infiltration gallery
|  | 1 | RANDAL'S RANCHETTE MUTUAL WATER CO. | Public Utility | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
| y | 1 | REDCREST WATER WORKS | other | P.O. BOX 282 REDCREST, CA 95569 | n | y |  | 35 | Monthly/ Annual Flat Rate | Unfamiliar; interested | [19 empty] | 1 | 1 | Redcrest, CA | Humboldt | North Coast, Region 1 | 48542 | n | 100 | SW | IN - Chadd Creek - raw |  |  | $0-50 | $0 - $50
| y | 1 | REDWAY C.S.D. | CSD | P.O. BOX 40 REDWAY, CA 95560 | y | y |  | 687 | Monthly/ Annual Flat Rate | Familiar; not a participant | [20 empty] | 1 | Redway, CA | Humboldt | North Coast, Region 1 | 37778 | n | 1500 | SW | IN - Eel River Infiltration Gallery - raw |  |  | $50-100; Res. $60.00 goes by use; Commercial $64. per month and goes up by use. | $51 - $100 |  | The District’s water system consists of two water sources, a conventional filter water treatment plant, three storage facilities, two pressure reduction vaults, and one booster pump station, as well as the transmission and distribution lines, many of which were installed prior to 1950. There are presently 600 service connections. The sources of water are the South Fork of the Eel River (surface water) and an unnamed spring (ground water). The water treatment plant design capacity is 460,000 gallons per day. The water permit allows for a draw of 1.05 CFS. The spring source is limited to .123 CFS, and 52 AC-FT per year. The maximum production for the spring is 46,000 gallons per day. The total capacity of the three storage areas is approximately 380,000 gallons. Additional storage capacity is indicated for fire safety during high use periods, which coincide with the highest fire danger seasons. There are areas within the district that are in the planning stages of subdivision; the developer would have to provide the needed additional storage capacity to enable the District to provide services to numerous additional customers Redway CSD’s water system consists of two water sources, an infiltration gallery in the South Fork of the Eel River and an unnamed spring, which is “inactive”. The Redway CSD’s total storage capacity is approximately 735,000 gallons in the residential area and 100,000 gallons in the Meadows Industrial Park. The District maintains approximately 25 miles of distribution piping, which is reported to have inadequate pressure in portions of the system during fire flows. The Redway CSD completed a project to address water system deficiencies in 2009. The District received funding through DDW and upgraded piping and valving to improve the operation and performance of the water treatment system and rehabilitated the Eel River intake. According to WaterWorks Engineers (WWE), Redway CSD Water and Wastewater Systems Capacity Analysis, 2014, “(t)he water treatment plant is limited by the design flows of the water intake pumps and booster pumps, and the pretreatment system to a capacity of 450 gpm. At the current Maximum Day Demand of 494,000 gallons, the water plant has to run 18.3 hours per day at its full output of 450 gpm in order to provide this volume of water. This should be viewed as essentially at capacity, because the plant is not staffed 24 hours per day, and while the bulk of the treatment process is automated, it is not designed for complete un-manned operation. Depending on the demand of significant new connections to the water system, the (Water Treatment Plant) capacity would need to be increased.” “It is the opinion of WWE that water treatment system is currently at capacity, and the water storage and distribution system is already struggling to meet the demands of existing connections. These issues should be addressed before substantial additional service connections are made.” | Fair condition/ Upgrades planned/ identified | [8 empty] | According to the Redway CSD Water and Wastewater Systems Capacity Analysis, WWE 2014, “(t)he most limiting facility at the treatment plant currently is the sludge dewatering process. Dewatering capacity is currently sufficient during the dry weather season, but not during the wet-weather season.” “The next item of concern is the peak hour wet weather flow hydraulic capacity of the piping downstream of the secondary clarifier overflow weir. Instantaneous flow above approximately 665 gpm will submerge the weir. This can be alleviated by upsizing the piping downstream of the clarifier from 8-inch to 10-inch, but this is not critical for short-term operation. “ “The last item of concern is the existing oxidation ditches apparent inability to denitrify at a level that will be necessary to achieve an anticipated future 10 mg/L nitrate limit. The existing WWTP may be able to meet this limit by closely monitoring immersion of the existing brush aerator and other process parameters, but it appears to be already close to its treatment capacity even if denitrification performance is optimized.” “Several options exists for improving the denitrification capacity of the plant, including 1) supplementing the existing oxidation ditch with a pre-anoxic basin and internal mixed liquor recycle pumping provisions, 2) installation of a new oxidation ditch in parallel to the existing oxidation ditch, or 3) installation of a new, stand-alone oxidation ditch and re-tasking of the existing oxidation ditch to an ancillary facility such as emergency overflow, aerobic digester, etc. However, all of the options would be costly, and would require procurement of funding assistance in order to implement.” In particular, the Redway CSD Water and Wastewater Systems Capacity Analysis concludes that “The existing wastewater treatment plant may not be capable of complying with what is believed to be a forthcoming effluent discharge limit for nitrate of 10 mg/L, at current wastewater flows and loads. It is very unlikely that it would be able to meet the 10 mg/L limit with increased flows and loads.” | Fair condition/ Upgrades planned/ identified
y |  | 1 | REDWOOD HEIGHTS WATER ASSOCIATION | Mutual | 190 S. ORCHARD AVE., STE B220, VACAVILLE, CA 95688 | n | n | y | 17 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 2 | Redwood Heights Dist. in Cazadero, CA | Sonoma | North Coast, Region 1 | 49886 | n | 30 | GW | Well | [8 empty] | 0 | 1. Total coliform monitoring and reporting violation for 3/14 2. Total coliform monitoring and reporting violation for May 2017 | 1. Total coliform monitoring and reporting violation for 3/14 2. Total coliform monitoring and reporting violation for May 2017 | D | 1. NOV: failing to divert surface runoff to prevent drainage from sludge treatment and storage sites | 1. 3/10/17 | septic | individual systems (17) | Adequate
y |  | 1 | REDWOOD PARK C.S.D. | CSD | P.O. BOX 650 KLAMATH, CA 95548 | n | n | y | 44 | uniform rate schedule | Unfamiliar; disinterested |  | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Redwood Park, CA | Del Norte | North Coast, Region 1 | 27200 | n | 200 | GW | Well (3) |  |  | 0-50 | $0 - $50 |  | The RPCSD water system facilities include: one 60 foot deep groundwater well, a gravity fed pipeline distribution system, one 15 horsepower pump and two redwood storage tanks including one 60,000 gallon and one 150,000 gallon tank. The RPCSD water is metered, and is typically supplied to homes through ¾-inch supply lines. The District’s 150,000 gallon redwood water tank is leaking and needs replacement. Some of the system’s piping currently needs repair/replacement and the District needs additional storage capacity to adequately provide water in an emergency. | Fair condition/ Upgrades planned/ identified | [8 empty] | The RPCSD’s wastewater system consists of 0.25 miles of six inch mains, a gravity collection system, two lift stations, Imhoff tank, and five-acre leach field. The wastewater treatment facility is located adjacent to and east of the District Boundary and has a capacity of 15,400 gallons per day (RPCSD, 2009). The wastewater system adequately serves District residents at this time. The sewer mains will need replacement in the future. | Adequate
y | y | 1 | REDWOOD VALLEY COUNTY WATER DISTRICT | Water Dist | P.O. BOX 399 REDWOOD VALLEY, CA 95470 | y | y | n | 1335 | The rates include a meter charge based on the size of the meter plus a usage charge. Domestic water customers are assessed on a five-tier usage schedule ranging from $3.75 to $5.50 per 1,000 gallons. Agricultural customers are charged a flat $0.69 per 1,000 gallons. (went into effect in 2010) | Familiar; lack resources to participate |  | 0 | 2 | 2 | 2 | 3 | 3 | 3 | 2 |  | 3 | 3 | 2 | 2 | 3 | 0 | 1 | 2 | 2 | 3 | 1 | Redwood Valley, CA | Mendocino | North Coast, Region 1 | 60692 | n | 3617 | SW | In- Pump station caisson/ WTP Raw |  |  | 0-50 | $0 - $50 |  | The RVCWD’s water supply comes from Lake Mendocino. A pump station located at the Lake pumps water to a holding reservoir 4.5 miles from the Lake. The holding reservoir has a capacity of 68 AF. During typical demand, water is pumped to the reservoir from the lake at night to take advantage of lower electricity rates. From there, domestic water is delivered by gravity flow to the water treatment plant. The plant can treat up to 1.7 mgd. Treated potable water is pumped to six covered steel tanks with a total volume of 1.85 million gallons. Water flows by gravity fro m these tanks to customers. Irrigation water flows by gravity to the irrigation distribution system. During periods of high demand gravity flows are augmented by pressure flows from the lake pumps. The RVCWD’s water supply consists of a largely un-exercisable right to divert up to 4,900 AF directly from Lake Mendocino between November 1 and April 30 of each year, and divert surplus water supplies from RRFC and the Sonoma County Water Agency. Water diversions made according to the RVCWD’s Lake Mendocino water right can only occur in instances when stream flows in the Russian River main stem ( as measured at the confluence of the East and West forks) exceed 150 cfs and Lake Mendocino storage exceeds 72,000 acre-feet. This represents a relatively narrow window of opportunity that can be as much as 70 days in wet years, but as little as one or two days in dry years. Because of the uncertain supply, the RVCWD is currently under court-ordered moratorium for domestic connections and a board-initiated moratorium for irrigation connections. | Uncertain water supply
y |  | 1 | Reservation Ranch | other | 370 Sarina Road, Smith River | y | n | don't know | 21 | We do not have rates. This is a small, private system serving owner and employees. | Unfamiliar; disinterested |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 0 | 2 | 2 | Reservation Ranch, private system | Del Norte | North Coast, Region 1 | 42944 | n | 50 | GW | well |  |  | n/a | [8 empty] | C | 1. Notice of Violation and CA WC Section 13267 Order for Technical Reports: unlawful discharges of waste into waters of the state (violations of Conditional Waiver of Waste Discharge Requirements for Existing Cow Dairies in the NC Region). 2. Notice of Violation of CWC Section 13267 Order for Technical Reports, Staff's recommendation. Failed to submit technical reports 4/6/17 3. NOV: CWC Section 13267 Order for Technical Reports | 1. 1/9/2017 | septic
y | y | 1 | RESORT IMPRVMT. DIST. #1 | Resort Imp Dist |  | y | y | y | 470 | montly/ annual flat rate; increasing block (graduated) schedule; wastewater is a monthly flat rate for residential and commercial users, and water is billed under a tiered use structure, so monthly bills vary tremendously based upon water use. | Familiar; lack resources to participate | Funded | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | Shelter Cove, CA | Humboldt | North Coast, Region 1 | 41140 | n | 324 |  |  |  |  | 100-150 | $101 - $150 |  | The RID water source consists of two active surface water spring intakes (Rick Spring and Upper Telegraph Creek), a seasonal standby surface water spring intake (Lower Telegraph Creek), and two standby wells. During summer months when demands are high, the District is required to maintain environmental flows within Telegraph Creek and is allowed to withdraw at Lower Telegraph Creek at a point prior to the water’s infiltration into beach sands. The source capacity of the District is approximately 508 gpm (0.732 MGD), well over current maximum day demands (230 gpm). The treatment capacity of the plant is 350 gpm, or 0.504 MGD. Water service within the RID is generally very good.The district maintains 12 storage tanks (welded steel and redwood) ranging in size from 0.03 MG to 1 MG. The distribution system consists of approximately 44 miles of water main of varying size. The majority of the distribution system is asbestos cement (AC) pipe, but some above ground cross-country steel and polyvinyl chloride (PVC) is also present. The District is in the process of locating additional source capacity. The RID has identified sites for new water wells, several of which have been approved by the state for service. The RID Board has approved funds for the exploration of five new well sites to be located in regions of the upper Cove where successful well sites have been established and geologic conditions are similar (Resort Improvement District #1 General Manager’s Report, February 2012). The District’s water supply system consists of a diversion facility and treatment plant on Telegraph Creek. The distribution system has been extended throughout the District and contains 18 storage tanks and 10 booster pump stations. Although the distribution system was installed District-wide, the initial water appropriation rights were not sufficient to meet projected demand for full build-out. | Uncertain water supply | [7 empty] | sewer | The service includes wastewater collection, treatment, and disposal. RID’s collection system incorporates both gravity mains and nine lift stations. The wastewater treatment plant (WWTP) consists of coarse screening, two oxidation ditches, two clarifiers, and chlorination/de-chlorination facilities. Based on existing flows, the District is approximately at 59% of dry weather treatment capacity and approximately 78% wet weather capacity at its WWTP. The District is currently under an Administrative Civil Liability Order due to the District’s inability to meet treatment requirements. In essence, the influent to the treatment plant is so diluted, it is virtually impossible to meet these requirements. The District last developed a Master Plan Update for its wastewater treatment and disposal facilities in 1997, which outlines necessary improvements to meet different forecasted growth scenarios. The District also developed a ten-year capital improvement program in 2007 to address required maintenance and upgrades to their wastewater system. The District instituted an I&I rehabilitation program in February 2008 as a compliance project in response to Administrative Civil Liability Order No. R1-2007-0009. The District has continued to complete inspections and point repairs of the collection system, including improvements to manholes. According to the approved Waste Discharge Requirements/ Permit (R1-2015-0017), although the design peak daily wet weather flow was exceeded in 2012 (0.818 mgd), the facility remained below the design peak daily wet weather flow of 0.77 mgd for the most recent 4 years (0.568 mgd). | Adequate
|  | 1 | White Deer Lodge Water System (formerly Ridge Water System) | Other |  |  |  |  | 7 | [24 empty] | Mendocino | North Coast, Region 1 | 32667 | n | 20 | GWP | purchase groundwater from Ridgewood Water System
|  | 1 | RIDGEWOOD WATER SYSTEM | Mutual | 16200 N HWY 101 WILLITS,CA 95490 |  |  |  | 167 | [24 empty] | Mendocino | North Coast, Region 1 | 32667 | n | 270 | GU | Springs (3), well | [8 empty] | 0 | 1. Nitrate and nitrite monitoring and reporting violations 2. Failure to comply with the Condition #17 of Domestic Water Supply Permit No. 02-03-02P23002 | 1. 9/17/14 2. 12/13/12
|  | 1 | RIEBLI MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 42958 | n
|  | 1 | RINCON VALLEY MOBILE ESTATES | Other | P.O. Box 7 NOVATO, CA 94948 |  |  |  | 230 | [24 empty] | Sonoma | North Coast, Region 1 | 44390 | n | 460 | GW | Wells (2)
y | y | 1 | RIO DELL, CITY OF | City | 675 WILDWOOD AVE. RIO DELL, CA 95562 | y | y | y | 1233 | There is a base charge and a volume charge, monthly. | Familiar; regular participant | Funded | 3 | 1 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 1 | 1 | 2 | 2 |  | Rio Dell, CA | Humboldt | North Coast, Region 1 | 47639 | n | 3174 | SW | Eel River - raw |  |  | $61.83/month water and $71.39/month sewer | $101 - $150 | The City’s water supply comes from a recently completed infiltration gallery in the South Fork of the Eel River. The production capacity of the gallery is tied to water levels within the river, such that in the winter the pumps can deliver around 700 gpm, but in the summer production falls to about 550 gpm (0.792 MGD). Water is pumped to treatment for filtration and disinfection before entering the City’s distribution system. The Metropolitan Wells project provided a state-of-the-art filtration system upon the City's old well site and added an additional layer of water security for the City. Moving forward, the City is working on obatinaing State grants through Proposition 1 to rehabilitate aged water lines and replace water storage systems. | The City’s water supply comes from a recently completed infiltration gallery in the South Fork of the Eel River. The production capacity of the gallery is tied to water levels within the river, such that in the winter the pumps can deliver around 700 gpm, but in the summer production falls to about 550 gpm (0.792 MGD). Water is pumped to treatment for filtration and disinfection before entering the City’s distribution system. The City has two pressure zones served by four tanks ranging in size from 100,000 gallons to 500,000 gallons for a total combined storage capacity of 1.1 million gallons. The distribution system contains approximately 11 miles of pipe, of which 5 miles were replaced with 10” HDPE pipe under the City’s infrastructure rehabilitation project. The remaining distribution system ranges in size from 4 inches to 6 inches and consists mainly of AC pipe. The City has recently invested heavily in upgrading its water system following a declared water emergency in 2001 when the City’s water supply began to fail. Since then, they have received $5.0 million in grant funds to rehabilitate the water distribution system city-wide and $1.0 million in grant funds and a loan in the amount of $2.3 million to construct a new infiltration gallery and water treatment plant. The new treatment plant has a design capacity of 700 gpm. | Good condition |  |  | 1. Category 2 Pollutant (Effluent Violation for Group 2 Pollutant) | 1.15.2019 |  |  |  |  | The city has identified several wastewater facility improvement projects and continues to seek grant funding. The first is to address the collection system’s high inflow and infiltration (I/I). Surface stormwater and seasonally high groundwater is a significant contributor to I/I in Rio Dell. Poor drainage in areas of the city causes ponding and flooding leading to I/I. The city has been working to identify areas of the city where stormwater ponding and flooding has been historically problematic and is near wastewater pipes and therefore directly contributing to I/I. The city reports they are actively seeking grant funding to complete a comprehensive Sanitary Sewer Evaluation Study (SSES). | Fair condition/ Upgrades planned/ identified | The City is in the process of a drainage project for repairs and upgrades to severely degraded or inoperable portions of the stormwater system in various locations in the city, including culvert replacement and repair, completed in 2018. The City reports that future projects are planned, but still in need of financing.
y |  | 1 | (Russian) RIVER ESTATES MUTUAL WATER COMPANY | Mutual | 151 LAWS AVENUE UKIAH, CA 95482 | n | y | y | 82 | uniform rate schedule | Familiar; not a participant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Russian River Estates, Ukiah Valley, CA 95482 | Mendocino | North Coast, Region 1 | 19356 | n | 250 | GW | Wells (3) |  |  | 61-80 | $51 - $100 |  | The Company owns and maintains 2 active wells, 1 standby well, and approximately 9,000 feet of pipeline. In addition, the Company owns and operates two storage tanks. They participate in cooperation with Willow County Water District for shared facilities andadministrative and operations services. | Adequate
|  | 1 | Riverbend Mobile Home Park | other | 45630 Highway 36 BRIDGEVILLE,CA 95526 |  |  |  | 28 | [24 empty] | Humboldt | North Coast, Region 1 | 28277 | n | 60 | GW | Well | [8 empty] | 0 | 1. Failure to monitor for coliform bacteria in drinking water 2. Failure to monitor for coliform bacteria in drinking water | 1. 1/11/2017 2. 2/22/17
y | y | 1 | RIVERSIDE CSD | CSD | 790 Centerville Rd FERNDALE, CA 95536 | y |  |  | 99 | monthly/ annual flat rate | [22 empty] | Ferndale rural areas from Port Kenyon to Centerville Road. | Humboldt | North Coast, Region 1 | 52679 | n | 293 | GW | Wells (4) | [5 empty] | The District’s water source consists of three wells with a maximum production capacity of approximately 74,000 gallons of water a day. The District water source consists of artesian springs and wells with a maximum production capacity of approximately 60,000 gallons of water a day.Water service within the Riverside service area is generally good. Current peak water use is at approximately 62% of available production capacity. The District’s deep well can only be used as an auxiliary well due to high manganese content. The District does not currently have any fire hydrants and is not capable of supporting fire suppression. |  | The District’s deep well can only be used as an auxiliary well due to high manganese content.
|  | 1 | ROGINA WATER COMPANY INC. | PUC | PO Box 310, Talmage, CA 95481 1850 Talmage Road, Talmage, CA | y |  |  | 985 |  | Familiar; not a participant | [21 empty] | Talmage, CA | Mendocino | North Coast, Region 1 | 73523 | n | 3500 | [7 empty] | The Company system consists of 5 wells, 4 large tanks for a combined storage of 1.3 million gallons, 2 booster systems, and over 30 miles of main lines made of steel, asbestos cement &plastic. The Rogina Water Company reports that its water supply is sufficient through 2050. In the interim, the Company is planning to develop new wells in the Talmage area. Water conservation is promoted through informational bill inserts and water saving yard brochures to new homes. Rogina Water Company has grown over the years with the development of new homes, and provision of water service to areas with limited water availability on the eastside of the Russian River. The Company plans to build and expand with growth in this area. | Good condition
|  | 1 | ROLLING OAKS ROAD ASSOCIATION | Other | [29 empty] | Sonoma | North Coast, Region 1 | 49726 | n
|  | 1 | ROSELAND MOBILE HOME PARK | other | 1355 Sebastopol Road SANTA ROSA, CA 95407 |  |  |  | 70 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 130 | GW | Wells (2)
y | y | 1 | RUSH CREEK MUTUAL WATER SYSTEM | Mutual | P.O. BOX 18480 WEAVERVILLE, CA 96093 | y | y | y | 37 | Increasing block (graduated) rate schedule | Familiar; regular participant | Unfunded | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | Rush Creek Estates, Rush Creek Drive, Trinity County | Trinity | North Coast, Region 1 | 40455 | n | 80 | SW | Rush Creek - raw |  |  | 51-100 | $51 - $100
y |  | 1 | RUSSIAN RIVER COUNTY SANITATION DISTRICT | Sanitary Dist | (LOCATION: 18400 NEELEY RD., VACATION BEACH, CA (MAILING:) 404 AVIATION BLVD., SANTA ROSA, CA 95403 | y | y | y | 1,000 - 5,000 | monthly/ annual flat rate | Familiar; regular participant |  | 1 | n/a | n/a | n/a | 3 | 3 | 0 | 0 | 1 | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | The RRCSD includes the unincorporated areas of Rio Nido, Guerneville, Guernewood Park and Vacation Beach | Sonoma | North Coast, Region 1 | 46037 | n | [5 empty] | Property tax charges, $1484 per ESD (1 unit) wastewater only; estimate 100-150 | $101 - $150 | [10 empty] | sewer | In the past, projects for wastewater treatment systems have not ranked high enough to receive IRWM funding, even though they are serving DACs. Wastewater treatment projects don't include a broad array of partners and the projects are not particularly compelling in a competitive environment. Concerns/challenges with sustainability/state continuing funding of IRWM programs; our wastewater projects do not have collaborations with other entities and are not attractive projects for the IRWM Program. The wastewater projects we submitted did not get funded. | Fair condition/ Upgrades planned/ identified |  |  | 1
|  | 1 | RUSSIAN RIVER MUTUAL WATER CO. | Mutual | P.O. box 1580 HEALDSBURG, CA 95448 |  |  |  | 30 | [24 empty] | Sonoma | North Coast, Region 1 | 57639 | n | 84 | GW | Well
| y | 1 | RUTH LAKE MARINA AND RECREATION AREA | CSD |  | y | y |  | 0-25 |  | Unfamiliar; disinterested | [15 empty] | 1 |  |  |  | 1 |  | Ruth Lake Campground and Marina in Mad River, Trinity County. | Humboldt | North Coast, Region 1 | 25395 | n
| y | 1 | SALYER HEIGHTS W.S., INC | Public Utility | P.O. BOX 156 SALYER, CA 95563 | n | n |  | 42 | Monthly/Annual Flat Rate | Familiar; infrequent participation | [20 empty] | 1 | Salyer Heights, CA | Trinity | North Coast, Region 1 | 35104 | n | 82 | SW | Huckleberry and Shaber Creeks, IN - raw |  |  | $180 a year | $0 - $50 |  |  |  |  | B | 1. Failure to comply with combined filter effluent turbidity performance standards | 1. 2/17/17
|  | 1 | SALYER MUTUAL WC (FORMERLY RIVERVIEW AC) | Mutual | P.O.Box 484 SALYER, CA 99563 |  |  |  | 64 |  | Familiar; infrequent participation | Funded | [21 empty] | Trinity | North Coast, Region 1 | 35104 | n | 201 | SW | Trinity River infiltration well, IN - raw
| y | 1 | SANTA ROSA MOBILE ESTATES | other | P.O. Box 176 Sebastopol, Ca 95473 | n | y |  | 141 | [23 empty] | Santa Rosa Mobile Estates Mobile Home Park located in Santa Rosa, Ca. / Sonoma County | Sonoma | North Coast, Region 1 | 49306 | n | 420 | GW | Wells (3)
y |  | 1 | SAWYERS BAR COUNTY WATER DISTRICT | Water Dist |  | n | y | n | 30 | monthly/ annual flat rate | Familiar; lack resources to participate |  | 1 | 3 | 3 | n/A | 3 | n/a | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | Sawyer's Bar, CA | Siskiyou | North Coast, Region 1 | 32500 | n | 50 |  |  |  |  | Over $150 | > $150 | [14 empty] | 1
|  | 1 | Scotia CSD | CSD | po Box 245, Scotia, CA 95565 |  |  |  | 308 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Humboldt | North Coast, Region 1 | 48542 | n | 850 | SW | IN - Eel River, raw | [5 empty] | The Scotia CSD water supply comes from an infiltration gallery in the Eel River that supplies separate domestic water and raw water fire systems. In January 2016, the Scotia CSD adopted a resolution approving a letter of intent to accept all dedicated facilities and properties from the Town of Scotia, LLC, to provide utility and other services to the former mill town. The Scotia CSD has since adopted rates for water and sewer services and agreed to assume responsibility, accept the dedicated properties, and own and operate the systems thereafter. These rates include funding to carry out the necessary improvements to the water and wastewater systems, including a new water treatment plant above the 100-year flood elevation. | Fair condition/ Upgrades planned/ identified | The Scotia CSD WWTP is located within the 100-year floodplain. The treatment capacities of multiple unit processes within the facility are exceeded even by average day maximum month flows (Winzler & Kelly, 2006). However, under current conditions the three treatment ponds at the WWTP provide the necessary treatment to meet current permit conditions (SHN, 2007). In 2006, there was concern that the facility would not meet the secondary treatment standards for treatment. PALCO requested the facility be placed under a cease and desist order that set forth a time schedule for compliance with permit requirements relating to treatment. The cease and desist order was rescinded in April 2012 and a new permit was issued (ORDER NO. R1-2012-0065). The new permit states that “(a) hydraulic study was conducted during the term of the permit and determined that the design average dry weather flow of the WWTF is 1.0 MGD. Annual average flows at the Facility are approximately 0.200 MGD.” The Scotia WWTP currently discharges to percolation ponds adjacent to the Eel River during the summertime discharge prohibition period. The town will likely have to find alternative methods for summertime disposal, as percolation ponds on the Eel River are becoming more difficult to permit with time. As indicated above, the Scotia CSD has assumed responsibility for the wastewater system and is responsible for carrying out the LAFCo conditions of approval for the formation of the Scotia CSD, which specifies certain wastewater system improvements. | B | 1. Failure to comply with combined filter effluent turbidity performance standards | 1. 7/1/16
|  | 1 | SEA RANCH SANITATION ZONE | Sanitary Dist | [29 empty] | Mendocino | North Coast, Region 1 | 62750 | n
|  | 1 | SEA RANCH WATER COMPANY,THE (PUC) | Public Utility | [29 empty] | Mendocino | North Coast, Region 1 | 62750 | n
y |  | 1 | SEAFAIR ROAD AND WATER COMPANY | other | 45341 Mar Vista Drive MENDOCINO, CA 95460 | n | n | y | 31 | Monthly / annual flat rate; overage charge if people go over 7,500 gallons per month, otherwise flat rate | Familiar; lack resources to participate |  | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | Point Cabrillo Drive and Mar Vista in city of Mendocino, near Russian Gulch State Park | Mendocino | North Coast, Region 1 | 51277 | n | 50 | GW | Wells (7) |  |  | 100-150 | $101 - $150 | a water purification system, | The Company owns and/or maintains 4 active wells, 2 active standby wells, approximately 1-1.5 miles of pipeline, a water purification system, and a 10,000 gallon storage tank. | Adequate | We use surface water/shallow wells so sometimes we have biological contamination | [10 empty] | 1
| y | 1 | SEAWOOD ESTATES MUTUAL WATER | Mutual | P.O. Box 561 (161 Westgate Drive) TRINIDAD, CA 95570 | n | y |  | 23 | Monthly/ Annual Flat Rate | Unfamiliar; interested | [17 empty] | 1 | 1 | 1 |  |  | Humboldt | North Coast, Region 1 | 50417 | n | 60 | SW | IN - Parvin Creek - raw, Savage Creek - raw |  |  | 100/ residence/ mo | $51 - $100 |  |  |  |  | B | 1. Failure to comply with combined filter effluent turbidity performance standards | 1. 10/21/14
y | y | 1 | SEBASTOPOL, CITY OF | City | 714 JOHNSON STREET SEBASTOPOL, CA 95472 | y | y | y | 2900 | Increasing block (graduated) rate schedule | Familiar; infrequent participation | Unfunded | 3 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 3 | 1 | 2 | 1 | 0 | 0 | 1 | 3 | 2 |  | Sebastopol, CA | Sonoma | North Coast, Region 1 | 99141 | n | 7527 | GW | Wells (4) |  |  | 100-150 | $101 - $150 | Arsenic - Blending and Sorb 33 granular iron oxide media treatment system |  |  | PCE contamination | [6 empty] | sewer
|  | 1 | SEQUOIA WATER COMPANY | other |  |  |  |  | 4 | [23 empty] | Gravenstein Highway, Sebastopol 95472 | Sonoma | North Coast, Region 1 | 52396 | n | 100 | GW | Well (1) |  | 1
|  | 1 | SERENO DEL MAR WATER CO. | other | [29 empty] | Sonoma | North Coast, Region 1 | 49732 | n
y | y | 1 | SEYMOUR'S MUTUAL WATER SYSTEM | Mutual | HCR2 Box 4793 TRINITY CENTER, CA 96091 | y | n | y | 28 | monthly/ annual flat rate | Familiar; regular participant |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Seymour's Mountain Ranches Mutual Water System Subdivision | Trinity | North Coast, Region 1 | 32321 | n | 25 | GW | Springs (3) - raw |  |  | 0-50 | $0 - $50
|  | 1 | SHADOW MOUNTAIN MHP | other | P.O. BOX 11158 SANTA ROSA, CA 95406 |  |  |  | 71 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 100 | GW | Wells (3)
|  | 1 | SHAMROCK MOBILE HOME PARK | other | 6418 North Old Redwood Highway SANTA ROSA, CA 95403 |  |  |  | 127 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 188 | GW | Well | [8 empty] | 0 | 1. Disinfection by-product monitoring reporting violation for 2010 - 2012 | 1. 3/11/13
y | y | 1 | SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | other | P.O. BOX 732 YREKA, CA 96097 | n | y | y | 24 | monthly/ uniform rate schedule | Unfamiliar; interested |  | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 3 | 0 |  | 2 | [6 empty] | Greenhorn Road and Bennett Drive, Yreka | Siskiyou | North Coast, Region 1 | 25493 | n | 50 | GW | Well |  |  | 51-100; cost includes association fees also - average is $70 to $79 per month per site | $51 - $100 | [14 empty] | 1
|  | 1 | SHASTINA MOBILE ESTATES | other | [29 empty] | Siskiyou | North Coast, Region 1 | 18125 | n
y |  | 1 | SHORELANDS ROAD & WATER COMPANY | other | P.O. BOX 722 MENDOCINO, CA 95460 | y | n | y | 47 | monthly/ annual flat rate; In addition we charge by usage as a percentage of the volume costs. | Unfamiliar; interested |  | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | Small subdivision just north of Russian Gulch S.P. off of Point Cabrillo Drive, Fern Drive and Cypress Drive being the main streets. | Mendocino | North Coast, Region 1 | 51277 | n | 85 | GW | Wells (5) |  |  | 51-100 | $51 - $100
|  | 1 | SISKIYOU CO. ROLLING HILLS MWC | Mutual | 501 ARROYO DR. YREKA, CA 96097 |  |  |  | 95 | [24 empty] | Siskiyou | North Coast, Region 1 | 25493 | n | 300 | GW | Wells (2) | [8 empty] | A | 1. Total coliform bacteria 2. Total coliform monitoring and reporting violations for 2012 - 2013 | 1. 7/19/2016 2. 2/24/17
| y | 1 | SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system) | City | P. O. BOX 470, Weed, CA 96094 | y | n |  | 58 | Monthly/ Annual Flat Rate | Familiar; infrequent participation | [21 empty] | Weed and CSA 5 | Siskiyou | North Coast, Region 1 | 18125 | n | 142 | GW | Well |  |  | $0-50 | $0 - $50
y |  | 1 | Six Acres Water Company | Other | 87 Lile Lane CLOVERDALE, CA 95425 |  |  |  | 22 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cloverdale, CA | Sonoma | North Coast, Region 1 | 37411 | n | 66 | GW | Well | [8 empty] | A | 1. Failure to submit 2014 Annual Report to the Division 2. Inorganic, secondary, nitrate, nitrite, perchlorate, VOC, and SOC chemical monitoring and reporting violations for 2014 & 2015 3. Total coliform monitoring and reporting violation for November 2015 4. Compliance Order No. 02_18_16R_001 5. Total coliform monitoring and reporting violation for july - november 2016 6. Total Coliform MCL violation for April 2017 7. Total Coliform monitoring and reporting violation for October 2013 8. Monitoring and reporting violation for December 2012 | 1. 7/17/16 2. 1/22/16 3. 1/12/16 4. 3/30/17 5. 12/7/16 6. 6/2/17 7. 12/6/13 8. 2/12/13
| y | 1 | SMITH RIVER C.S.D. | CSD | 241 FIRST ST. SMITH RIVER, CA 95567 | y | y |  | 582 | increasing block | Familiar; infrequent participation | Funded | [5 empty] | 1 | [5 empty] | 1 | [7 empty] | 1 | Smith River, CA | Del Norte | North Coast, Region 1 | 42944 | n | 2569 | GW | Wells (4) |  |  | $0-50; $24 minimum charge, then $1.32 per 100 cubic foot afterwards within 0-2,000 cubic feet; over 2000 = $1.59 per cubic foot. | $0 - $50 | Water is treated with sodium hypochlorite and a sodium silicate additive is used. | The water system is supplied by four 40-foot wells that are approximately 100 feet from Rowdy Creek,upstream from Fred Haight Drive. The district’s total storage capacity is 900,000 gallons. Three main storage tanks have a 600,000-gallon combined storage capacity and five smaller storage tanks, located in proximity to various hill side subdivisions, have a 300,000-gallon combined storage capacity. The water system includes four 40-foot wells, two 225,000-gallon redwood storage tanks, three 100,000- gallon redwood storage tanks, and three smaller tanks that have a combined capacity of 125,000 gallons. There are four 25-horsepower pumps and 35-miles of eight-inch mainline for water distribution. Critical infrastructure needs include the replacement of the wooden storage tanks, secured tank foundations, and the installation of new fire hydrants. Additional main storage capacity is currently being added. According to the prior MSR, 25 miles of piping is made of asbestos cement and is in need of replacement. | Fair condition/ Upgrades planned/ identified
|  | 1 | SONOMA COUNTY CSA 41-FITCH MOUNTAIN | County Dist | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
|  | 1 | SONOMA COUNTY CSA 41-FREESTONE | County Dist | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
|  | 1 | SONOMA COUNTY CSA 41-JENNER | County Dist | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
y |  | 1 | SONOMA COUNTY CSA 41-SALMON CREEK | County Dist | 2300 County Center Drive - Suite B100 SANTA ROSA, CA 95403 | y | y | y | 99 | Increasing block (graduated) rate schedule, and monthly/ annual flat rate (sewer) | Familiar; regular participant |  | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 3 | 1 | 1 | 2 | 1 | 3 | 1 | Sonoma County and North Marin County | Sonoma | North Coast, Region 1 | 46037 | n | 327 | SW | Spring, Well |  |  | 51-100; Sewer only: 2017/2018 Rates: $997/ESD/year rate increase: between 4-5%/year | $51 - $100 |  |  |  |  | 0 | 1. Lead and copper monitoring and reporting violation | 1. 6/9/17 |  |  |  | sewer |  |  |  |  | 1
y |  | 1 | SONOMA COUNTY MUTUAL WATER COMPANY | Mutual | 439 sage court BENICIA,CA 95410 2280 Cazadero Highway CAZADERO, CA 95421 | n | y | y | 20 | monthly/ annual flat rate | Unfamiliar; disinterested |  | 1 | 2 | 1 | 1 | 3 | 3 | 1 | 0 | 0 | 2 | 2 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | Between 2000 Cazadero Hwy and 2420 Cazadero Hwy. | Sonoma | North Coast, Region 1 | 41389 | n | 40 | GU | Well |  |  | 0-50 | $0 - $50 |  |  |  |  | B | 1. Compliance order No 02_18_17R_008 2. Failure to complay with a Compliance Order May 2013 | 1. 6/23/17 2. 5/28/13
|  | 1 | SONOMA COUNTY WATER AGENCY | County Dist | 2300 County Center Drive - Suite B100 SANTA ROSA, CA 95403 |  |  |  | 99 |  | Familiar; regular participant | Funded | [21 empty] | Sonoma | North Coast, Region 1 | 46037 | n
|  | 1 | SONOMA MOUNTAIN COUNTY WATER DISTRICT | Water Dist | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
|  | 1 | SONOMA WEST HOLDINGS NORTH PLANT | Other | [29 empty] | Sonoma | North Coast, Region 1 | 99141 | n
|  | 1 | SOUNDS OF THE SEAS W. S. | Other | 3443 Patricks Point Drive, Trinidad, CA 95570 |  |  |  | 14 | [24 empty] | Humboldt | North Coast, Region 1 | 50417 | n | 104 | GW | Well (1) |  | 1
y |  | 1 | SOUTH CLOVERDALE WATER COMPANY | Other | P.O. Box 1111 CLOVERDALE, CA 95425 | n | n | y | 39 | monthly/ annual flat rate | Familiar; not a participant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cloverdale, CA | Sonoma | North Coast, Region 1 | 37411 | n | 90 | GW | Well |  |  | 51-100 | $51 - $100 |  |  |  |  | C | 1. Compliance order for violation of Section 116555 of the CA Health and Safety Code, which requires each public water system to have a reliable supply of water for its customers. | 1. 10/17/14
|  | 1 | SOUTH PARK COUNTY SANITATION DISTRICT | Sanitary Dist | (MAILING:) 404 AVIATION BLVD., SANTA ROSA, CA 95403 | [28 empty] | Sonoma | North Coast, Region 1 | 46037 | n
|  | 1 | STEWARTS POINT WATER SYSTEM | Other | [29 empty] | Sonoma | North Coast, Region 1 | 61786 | n
|  | 1 | STONEGATE MOBILE HOME PARK | Other | [29 empty] | Sonoma | North Coast, Region 1 | 65516 | n
|  | 1 | SUMMIT VIEW RANCH MUTUAL WATER CO. | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n
|  | 1 | SUNRISE MOUNTAIN MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 41389 | n
y |  | 1 | SUNSET PARK COMMUNITY | Other | 2963 Santa Rosa Avenue, #D-4 SANTA ROSA, CA 95407 | n | y | y | 55 | Increasing block (graduated) rate schedule; metered, based on City of Santa Rosa rates | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 1 | 2963 Santa Rosa Ave, SR, 95407 | Sonoma | North Coast, Region 1 | 46037 | n | [5 empty] | 0-50 | $0 - $50
y |  | 1 | SURFWOOD MUTUAL WATER CORPORATION | Mutual | PO Box 166 Mendocino, CA 95640 44901 Baywood Drive MENDOCINO, CA 95460 | n | n | y | 102 | increasing block (graduated) rate schedule | Unfamiliar; lack resources to investigate/participate |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | Surfwood Neighborhood, Mendocino | Mendocino | North Coast, Region 1 | 51277 | n | 160 | SW | IN, Jack Peter's Creek |  |  | 51-100 | $51 - $100 | filtered prior to distribution | Surface water is collected from Jack Peter’s Creek, stored, and filtered prior to distribution. | Adequate | The Safe Drinking Water Information System lists a number ofmonitoring violations, the most recent occurring in March 2018. The USEPAnotes severalmonitoring and reporting violation dated June 23, 2016 with compliance achieved in November 201633.The Surfwood Mutual Water Corporation noted that SWRCB Compliance Order 02-03-18r-001 was received March 2018 requiring additional water treatment to comply with TTHM and HAA5 maximum contaminate levels. A contract with BWS Municipal Water Group is inprogress (May 2018) to achieve compliance. | C | 1. MCL violations for Total trihalomethane (TTHM) and Haloacetic Acid (HAA5) | 1. 6/23/17
y | y | 1 | SWEETWATER SPRINGS CWD - GUERNEVILLE | Water Dist | P.O. Box 48 GUERNEVILLE, CA 95446 | y | y | y | 2663 | increasing block (graduated) rate schedule; We do bimonthly billing for water use charges and a base (flat) charge. We also have an annual assessment on the County tax bill. Regarding question 30, the current rates are not adequate but we have a plan to make them adequate; it may not be sufficient though. We monitor results annually. | Familiar; not a participant |  | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 2 | 1 | Guerneville, Monte Rio, Rio Nido, Villa Grande, Guernewood Park, Vacation Beach | Sonoma | North Coast, Region 1 | 45489 | n | 6116 | GW | wells (3) |  |  | 51-100 | $51 - $100 | Manganese and Iron removal is part of our treatment process. Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods. | [12 empty] | Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods.
y | y | 1 | SWEETWATER SPRINGS CWD - MONTE RIO | Water Dist | P.O. Box 48 GUERNEVILLE, CA 95446 | y | y | y | 1064 | increasing block (graduated) rate schedule; We do bimonthly billing for water use charges and a base (flat) charge. We also have an annual assessment on the County tax bill. Regarding question 30, the current rates are not adequate but we have a plan to make them adequate; it may not be sufficient though. We monitor results annually. | Familiar; not a participant |  | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 2 | 1 | Guerneville, Monte Rio, Rio Nido, Villa Grande, Guernewood Park, Vacation Beach | Sonoma | North Coast, Region 1 | 45489 | n | 3000 | GW | wells (2) |  |  | 51-100 | $51 - $100 | Manganese and Iron removal is part of our treatment process. Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods. | [12 empty] | Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods.
|  | 1 | SYLVAN HARBOR TRAILER PARK | Other | Humboldt | [28 empty] | Humboldt | North Coast, Region 1 | 50417 | n
y |  | 1 | TENNANT C.S.D. | CSD | 13515 TENNANT ROAD MACDOEL, CA 96058 | y | y | y | 97 | Monthly/ annual flat rate | Unfamiliar; disinterested |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | Tennant, CA | Siskiyou | North Coast, Region 1 | 31923 | n | 94 | GW | Well |  |  | 0-50 | $0 - $50 |  |  |  | we dont have any water problems
|  | 1 | TERRACE VIEW WATER SYSTEM | Other | [29 empty] | Sonoma | North Coast, Region 1 | 49726 | n
|  | 1 | TIMBER COVE COUNTY WATER DISTRICT | Water Dist | [29 empty] | Sonoma | North Coast, Region 1 | 41389 | n
y | y | 1 | TREASURE CREEK WOODS MWC | Mutual | HC 2 BOX 3970 TRINITY CENTER, CA 96091 | n | y | y | 36 | monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 0 | 1 | 3 | 3 | 2 | 1 | n/a | 0 | 0 | 2 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 1 | 3 | 2 | We service all subdivisions on the east side of state highway 3 in Coffee Creek, CA | Trinity | North Coast, Region 1 | 32321 | n | 34 | GW | wells (2) |  |  | $450.00 Annuallly. | $0 - $50 | [10 empty] | sewer
| y | 1 | Trinidad Extended Stay | Other | Humboldt | n | n |  | 50-100 | Included as part of monthly site rental | Unfamiliar; disinterested | [20 empty] | 1 | MidWay RV Park Humboldt county | Humboldt | North Coast, Region 1 | 50417 | n | 100-250
|  | 1 | TRINIDAD, CITY OF | City | P.O.BOX 1084 TRINIDAD, CA 95570 |  |  |  | 325 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Humboldt | North Coast, Region 1 | 50417 | n | 1000 | SW | In - Luffenholtz Creek raw water diversion |  |  |  |  | After being treated and chlorinated, water is stored in two redwood tanks, which are carefully monitored to keep the wood wet to avoid warping. Water lines distributetreated water to homes and businesses from the redwood storage tanks. Some out-ofcity residents are served from the line that carries water from the treatment plant to the tanks. These residents may experience a higher chlorine level than customers farther down the line, a problem currently under study. | Potable water for the City system is currently supplied from Luffenholtz Creek, half mile from the coast, and approximately a mile and a half from the City. The pumps located at the infiltration gallery that supply pressure to move water through treatment to the storage tanks were inundated with sediment a few years back. The pumps were rehabilitated, but have never worked as well as expected since their repair. The pumps should be capable of delivering 120 gallons per minute (gpm), but only deliver about 100 gallons per minute. The City of Trinidad has an operations and maintenance program that keeps the storage, treatment, and distribution systems in good condition. The storage tanks are regularly inspected and the steel bands tightened to prevent water losses. The City conducted leak detection testing on the distribution system in 2003 and tested all water meters in 2003. Major leaks detected have been repaired, and poorly functioning water meters are being replaced as funds become available. | Fair condition/ Upgrades planned/ identified | [8 empty] | Currently, the City of Trinidad is comprised of approximately 200 residences, all of which have individual on-site wastewater treatment systems. The maintenance of these systems is a responsibility that falls on the landowner. A large proportion of the existing on-site wastewater disposal systems are more than 20 years old and were either installed prior to permit requirements or prior to permanent record keeping. It is unknown whether systems in and around Trinidad are being maintained or functioning properly. Maintenance of septic systems is very important because it ensures the system is functioning properly, extends the life of the system and helps prevent system failure. Failing septic systems pose a huge problem for homeowners and the City as a whole. The City of Trinidad is in the process of implementing an Onsite Wastewater Treatment System (OWTS) Management Program to provide for sustainable development and better water quality protection, public health and safety and economic stability in our coastal community through improved management of onsite septic systems in Trinidad. | Regulatory - septic
| y | 1 | TRINITY CENTER M.W.C. . | Mutual | P.O. BOX 185 TRINITY CENTER, CA 96091 | n | y |  | 252 | Monthly/ Annual Flat Rate | Unfamiliar; interested | [5 empty] | 1 | 1 |  | 1 |  |  | 1 | 1 | [5 empty] | 1 | 1 |  | Trinity Center, CA | Trinity | North Coast, Region 1 | 32321 | n | 729 | SW | IN - Swift Creek - raw |  |  | 45 | $0 - $50
y | y | 1 | TRINITY CO. W.W. DIST #1 | County Dist | P.O. BOX 217 HAYFORK, CA 96041 | y | n | y | 535 | Increasing block (graduated) rate schedule; monthly/ annual flat rate | Familiar; regular participant | Funded | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hayfork, CA | Trinity | North Coast, Region 1 | 28553 | n | 1775 | SW | IN - Big Creek diversion - raw and Hayfork - raw |  |  | Water $29.25 min (with 500 cu ft) Sewer $25.00 per EDU | $51 - $100 | [10 empty] | sewer
y | y | 1 | TRINITY KNOLLS MUTUAL WATER COMPANY | Mutual | P.O. BOX 222 TRINITY CENTER,CA 96091 | y | y | n | 65 | Annual flat rate with additional charge for exceeding preset amount of usage | Unfamiliar; lack resources to investigate/participate |  | 0 | 1 | 2 | 2 | 1 | 1 | 2 | 0 | 0 | 3 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 1 | 3 Subdivisions, KOA Kampground and residences near Trinity Center, CA | Trinity | North Coast, Region 1 | 32321 | n | 45 | GW | Wells (7) |  |  | 51-100 | $51 - $100 | [14 empty] | 1
|  | 1 | TRINITY VILLAGE MUTUAL WATER CO. | Mutual | P.O. BOX 106 SALYER, CA 95563 |  |  |  | 189 | [24 empty] | Trinity | North Coast, Region 1 | 35104 | n | 200 | SW | IN - Hawkins Creek - raw, IN, Trinity River - raw - standby
| y | 1 | TRIUMPH LIFE CAMP (TLC) YOUTH SUMMER CAMP | Other | Humboldt | n | y |  | 0-25 | no charge for water, campground | [13 empty] | 1 | 1 | 1 |  |  |  |  | 1 | 1 | Triumph Life Camp | Humboldt | North Coast, Region 1 | 35000 | n | 0-50
y | y | 1 | TULELAKE, CITY OF | City | 591 Main Street, TULELAKE, CA 96134 | y | n | y | 437 | Monthly/ annual flat rate | Familiar; regular participant | Unfunded | 0 | 0 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | Tulelake, CA | Siskiyou | North Coast, Region 1 | 33909 | n | 1000 | GW | wells (2) |  |  | 51-100 | $51 - $100 | [10 empty] | sewer |  |  |  |  | 1
|  | 1 | Twin Hills Vineyard (formerly TWIN HILLS MUTUAL WATER COMPANY) | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 52396 | n
|  | 1 | Ukiah Valley Sanitation District | Sanitary Dist | 151 Laws Avenue, Ukiah CA, 95482 | [28 empty] | Mendocino | North Coast, Region 1 | 19356 | n
y | y | 1 | UKIAH, CITY OF | City | 300 Seminary Avenue UKIAH, CA 95482 | y | y | y | 4781 | Use based, billed monthlyy | Familiar; regular participant | Funded | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 |  | Ukiah, CA | Mendocino | North Coast, Region 1 | 19356 | n | 16185 | SW | Ranney Collector IN, wells (3) |  |  | 100-150 | $101 - $150 | Because of the nature of ground water in the Ukiah Valley, the only requirement that is necessary at our wells is the addition of a disinfectant to maintain safe potable water in the distribution system. | The City receives project water from Lake Mendocino, groundwater, and surface water. Based onthe 2010 Urban Water Management Plan the City has determined there is sufficient water supply to meet anticipated future demands.The Millview County Water District serves the northern portion of the sphere of influence excep tfor the Brush Street Triangle and the Masonite property. It has sufficient supply to serve its customers through 2015. A recent cease and desist order would reduce available supply by 785 acre-feet annually. The order is being contested, but should it be upheld the District would have difficulty supplying water in 2020 and beyond unless it can purchase additional Lake Mendocino water or find another source.The Willow County Water District has sufficient water to meet future demands for normal, singledry year, and multiple dry year scenarios. | Uncertain water supply | [8 empty] | The City provides wastewater services to about two-thirds of City residents. The other residents receive service from the Ukiah Valley Sanitation District (UVSD). The UVSD also serves the northern and southern portions of the proposed SOI. The City and UVSD have signed a participationagreement whereby the City agrees to provide operation and maintenance of the sewer system andwastewater treatment for the UVSD. For their part, the UVSD agrees to share the costs based onthe number of equivalent sewer service units (ESSUs).The wastewater treatment plant has a capacity of 3.01 million gallons per day (MGD) dry weatherflow, 6.89 MGD average wet weather flow, and 24.5 MGD peak wet weather flow. Recent capitalimprovements, completed in 2010 have expanded the capacity by 2400 ESSUs. Of the additionalcapacity 65 percent was allocated to the District (1,560 ESSUs) and 35 percent to the City (840ESSUs).As of January 31, 2012, the District has 1061 remaining of the 1,560 ESSUs and the City has542.39 remaining of its 840 share. | Adequate | The City maintains a system of surface and underground drainage facilities that drain into OrrsCreek, Gibson Creek, and Doolin Creek and eventually to the Russian River. Since there is nocentral trunk line to collect and convey stormwater to the Russian River, capacity of thestormwater system is unknown. The City has developed a Stormwater Management Plan to reducethe discharge of pollutants from urban runoff into creeks and the Russian River. The planaddresses several areas of concern, public education and outreach, public involvement andparticipation, illicit discharge detection and elimination, construction site runoff control, post-construction stormwater management, and pollution prevention.The Public Involvement andParticipation Programincludes development and implementation of ways to detect and eliminateillicit discharges to the storm sewer system. Construction runoff control could include siltfences and temporary stormwater detention ponds. Post-construction management consists ofpreventative actions such as protecting sensitive areas (e.g., wetlands) or the use of structuralbest management practices such as grassed swales or porous pavement. Pollution preventioninvolves developing and implementing a program for preventing or reducing pollutant runoff frommunicipal operations. Major flood areas include lands adjoining waterways, such as the Russian River and its tributaries in the south Ukiah and Hopland areas. |  |  | 1
|  | 1 | Ukiah City WWTP | City |  | y |  |  |  |  | Unfamiliar; disinterested | [21 empty] | City of Ukiah | Mendocino | North Coast, Region 1 | 19356 | n | [15 empty] | 1. Admin Civil Liability 2. Admin Civil Liability 3. Unauthorized Discharge and Order Conditions | 1. 6.7.2017 2. 1.24.2018 3.2.28.2019
y |  | 1 | Upper Russian River Water Agency | County Dist | 151 LAWS AVENUE, SUITE D, UKIAH, CA 95482 | y | y | don't know | 101-250 wastewater; 1001-5000 water | monthly/ uniform rate schedule; monthly/ annual flat rate | Familiar; lack resources to participate |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 2 | 1 | 0 | unincorporated Ukiah and Redwood Valleys | Mendocino | North Coast, Region 1 | 36346 | n |  | 0-50
| y | 1 | VALLEY FORD WATER ASSOCIATION | Mutual | P.O. BOX 271 VALLEY FORD,CA 94972 | n | y |  | 19 | Uniform Rate Schedule | Unfamiliar; disinterested | [14 empty] | 1 | [6 empty] | Village of Valley Ford | Sonoma | North Coast, Region 1 | 46319 | n | 40 | GW | Wells (3) |  |  | over $100 | $101 - $150
|  | 1 | VINEHILL VISTA MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 63859 | n
|  | 1 | WADDINGTON W.W. | other | 4009 GRIZZLY BLUFF RD. FERNDALE, CA 95536 |  |  |  | 24 | [24 empty] | Humboldt | North Coast, Region 1 | 38750 | n | 75 | GW | Well
|  | 1 | WAYSIDE GARDENS MOBILE HOME PARK | other | 2389 SANTA ROSA AVENUE SANTA ROSA, CA 95407 |  |  |  | 50 | [24 empty] | Sonoma | North Coast, Region 1 | 46037 | n | 75 | GW | Wells (2) | [8 empty] | 0 | 1. Tetrachloroethylene monitoring and reporting violation fourth quarter 2013 2. Tetrachloroethylene monitoring and reporting violation first quarter 2013 | 1. 3/17/14 2. 6/11/13
y | y | 1 | WEAVERVILLE C.S.D. | CSD | PO Box 1510 (716 Main St.) WEAVERVILLE, CA 96093 | y | y | y | 1594 | Uniform rate schedule | Familiar; regular participant | Unfunded | 1 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 0 | Weaverville, Douglas City | Trinity | North Coast, Region 1 | 40455 | n | 3554 | SW | IN - East Weaver Creek - raw, Trinity River - raw, West Weaver Creek - raw |  |  | 0-50 | $0 - $50 |  | We have had issues in the past with Disinfection Byproducts, We have just recently been questioned about the presence of pesticides and fertilizers in the water due to Cannabis grows. | Fair condition/ Upgrades planned/ identified
| y | 1 | WEAVERVILLE S.D. | Sanitary Dist | P.O. Box 1269 (242 Trinity Lake Boulevard) WEAVERVILLE, CA 96094 | y | n |  | 1513 | Monthly/ Annual Flat Rate | Familiar; infrequent participation | Funded | [20 empty] | Weaverville, CA | Trinity | North Coast, Region 1 | 40455 | n | 3600 |  |  |  |  | $0-50 | $0 - $50
y | y | 1 | WEED, CITY OF | City | P.O. BOX 470 WEED, CA 96094 | y | y | y | 1110 | Increasing block (graduated) rate schedule | Familiar; regular participant | Funded | 1 | 3 | 1 | 1 | 2 | 2 | 1 | 1 |  | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1 | 3 |  | Weed, CA | Siskiyou | North Coast, Region 1 | 18125 | n | 2963 | GW | Springs, Beaughan, wells (3) |  |  | 51-100 | $51 - $100 |  | On June 29, 2017 the City of Weed filed a complaint (COMP-#23422) to the Division of Water Rights and State Water Resources Control Board requesting assistance in addressing a dispute between the City of Weed and Roseburg Forest Products regarding the rights to 2.0 cfs of water from Beaughan Springs in the Shasta River basin. As an independent citizen group, Water for Citizens of Weed, California, we would like to file this complementary complaint in support of the City’s complaint and to provide some additional background and information. The Parent Complaint Number is COMP-23422 submitted 6/29/17. The child Complaint Number is COMP-23423 for your reference. | Uncertain water supply |  | 0 | 1. Total coliform monitoring and reporting violations | 2017-02-24 |  |  |  | sewer | [5 empty] | 1
y | y | 1 | WEOTT C.S.D. | CSD | P.O. BOX 218 WEOTT, CA 95571 | y | y | y | 128 | There is a monthly base rate that comes with a given volume of water that is included with the base rate. If usage exceeds this volume there is a standard charge for each volume of overage (or excessive use) unit. The overage unit is 150 cubic feet. So, for each 150 ft^3 feet of water beyond the base rate allotment, a standard charge per unit is added to the monthly base rate. Hopefully that made sense. | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 1 | 0 | Weott , CA 95571 + one state park campground located in close proximity to Weott | Humboldt | North Coast, Region 1 | 33438 | n | 364 | SW | IN - A Line, Mill Creek raw, B Line - Unnarmed Creek raw |  |  | 100-150; If there are no water usage overages, the average bill for combined water and wastewater is roughly $104. | $101 - $150 | The springs flow by gravity through two separate treatment and distribution systems – Line A and Line B. Line A has a treatment capacity of 37.7 gpm at the maximum allowable filter loading rate, and Line B has a treatment capacity of 47.7 gpm. Each treatment train has two pressure filters in series. Sodium hypchlorite is injected following filtration. Interties exist between the two systems within the distribution system. Treatment capacity totals approximately 85.4 gpm (0.123 MGD) and is therefore more limiting than source capacity. | WCSD’s water system consists of two surface water sources located across the Eel River and south of Bull Creek. The springs located on Mill Creek are permitted to produce 80 gpm, and the springs located on Corner and Deck Creek are permitted to produce 60 gpm. The springs flow by gravity to two treatment trains – the Mill Creek springs provide water to Line A, while the other springs provide water to Line B. The total rated capacity of these sources is approximately 0.202 MGD. Weott CSD’s water system is in fair condition and has historically suffered supply problems during summer months. The District has installed meters on all service connections, addressed some severe leaks in the system, and adjusted filter operations, such that the treatment plant can operate within the regulatory constraints. The District operates two pressure zones, each served by separate storage and distribution systems. Water storage consists of two tanks: a 79,000 gallon concrete tank and a new 90,000 bolted steel tank. One booster station is in operation to boost Line A following filtration to storage. The distribution system consists of approximately three miles of PVC, steel, and aluminum pipe varying in size from 3 inches to 4 inches. | Fair condition/ Upgrades planned/ identified | No, nothing unusual. Turbidity, especially seasonally, is a frustrating issue at times but that is about it and that is not unusual around here. | B | 1. Failure to monitor for coliform 2. Failure to comply with combined filter effluent turbidity performance standards | 1. 3/7/2013 2. 10/21/14 |  |  |  |  | “The Weott CSD’s wastewater collection system incorporates gravity mains and one lift station that direct wastewater to a community septic tank where preliminary treatment occurs. From here, raw wastewater flows through a recirculation tank and pea gravel filter, a chlorine contact basin, and dechlorination facilities. Disposal facilities consist of both a community leachfield and direct discharge to the South Fork Eel River, although the direct discharge disposal is not currently used. Sludge is dewatered and transported to the Humboldt County solid waste transfer station for landfill disposal. “The Weott CSD currently provides wastewater service to most areas within its service boundaries. The system currently has approximately 134 residential connections, and flows currently range between 14,000 gpd during dry weather and 30,000 gpd during wet weather. The facility has a permitted dry weather capacity of 30,000 gpd, and is therefore operating at approximately 47 percent of design capacity.” The wastewater treatment system was constructed between 1989 and 1991 and system improvements were made in 2000 under a USDA grant that included improvements to the lift station, chlorination/dechlorination equipment, and the gravel filter distribution piping. The system currently is operating well within its design capacity, and no system upgrades are planned other than typical maintenance. | Good condition
|  | 1 | WENDELL WATER COMPANY (PUC) | Public Utility | [29 empty] | Sonoma | North Coast, Region 1 | 52396 | n
y |  | 1 | WEST PARK PROPERTIES | other | P.O. Box 1902 CRESCENT CITY,CA 95531 2051 NORTHCREST DR. SPACE 35 CRESCENT CITY, CA 95531 |  |  |  | 42 | [23 empty] | 2051 Northcrest Dr. Crescent City Ca. | Del Norte | North Coast, Region 1 | 26544 | n | 112 | GW | Well
y | y | 1 | WEST WATER COMPANY (PUC) | Public Utility | 335 ELSE WAY CLOVERDALE, CA 95425 | y | y | y | 13 | some metered and some flat | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | n/a | n/a | 3 | 3 | 3 | 3 | n/a | 3 | 3 | 3 | 3 | 3 |  | 1 | 3 | 0 | 3 | 3 | West's tract | Sonoma | North Coast, Region 1 | 37411 | n | 40 | GW | Well |  |  | 51-100 | $51 - $100 |  | Need help searching for funding for system upgrades to become "compliant" | Fair condition/ Upgrades planned/ identified
|  | 1 | WESTERN MOBILE HOME PARK | other | 871 38TH AVENUE SANTA CRUZ, CA 95062 |  |  |  | 73 | [24 empty] | Sonoma | North Coast, Region 1 | 29250 | n | 225 | GW | Wells (2) | [8 empty] | C | 1. Cis-1,2-dichloroethylene and trichloroethylene monitoring and reporting violation for second quarter 2014. 2. Trichloroethylene and cis-1,2-dichloroethylene monitoring and reporting violation for the first quarter of 2013 3. Trichloroethylene MCL violation and domestic water supply permit No. 02-18-05P-4900791 violation | 1. 8/27/14 2. 6/11/13 3. 11/13/13
y | y | 1 | WESTHAVEN C.S.D. | CSD | PO BOX 2015 (446 6th Avenue #B) TRINIDAD, CA 95570 | y | y | y | 226 | uniform rate schedule | Familiar; infrequent participation | Funded | 3 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 1 | 1 | 2 | 0 | 3 | 1 | Moonstone / Westhaven California - near Trinidad | Humboldt | North Coast, Region 1 | 50417 | n | 490 | SW | IN - South Branch of Two Creek, raw, Tributary collector - raw, well, raw |  |  | 51-100; water only | $51 - $100 |  | The system is supplied by three small, spring-fed tributaries of Two Creek at the eastern edge of the community and a 100-foot deep well within the residential area. The creek source represents approximately 75% of the total source capacity, with the well accounting for the remaining 25%. During the system-upgrading project in the early 1990s, the District expended considerable resources in efforts to locate additional local water sources. Except for the well, no additional sources that could be developed in an economically feasible manner were located within the District. During this same time, an attempt by the District to develop a municipal well just outside the northeast boundary failed due to local political impasse. The District has installed meters on all residential connections recently, which has facilitated the District in identifying leaks and distribution system problems. Aside from inadequate source capacity, no serious deficiencies were identified through the DDW inspection. Many improvements have been made to system through IRWM program. Plans are also underway to upgrade the distribution system’s undersized water mains, increase storage capacity, and further explore additional sources of water. Development that has occurred within Westhaven has benefited from previously approved connections to the Westhaven CSD water system or has been approved with the use of individual onsite water systems. | Good condition | Surface water has very high levels of dissolved organic carbon during rainy weather, and we are on the north coast, hence the DBP issues.
|  | 1 | WESTPORT COUNTY WATER DISTRICT | Water Dist | 36970 Omega Drive, Westport, CA 95488 P.O. Box 55 WESTPORT, CA 95488 | y |  |  | 75 | tiered; water use in excess of 12,000 gallons per month (residential) is charged according to amount of usage | Familiar; infrequent participation | Unfunded | [20 empty] | Westport | Mendocino | North Coast, Region 1 | 55370 | n | 369 | SW | IN - Wages Creek, Well |  |  | The basic rate for water and sewer is $83.01 per month for each residential and commercial user. lthough the District has meters on each service, basic residential rates are based on a usage of 12,000 gallons per month. Water use in excess of 12,000 gallons per month is charged according to amount of usage. | $51 - $100 |  | A community treatment, storage, and distribution system was installed in 1976 using Wages Creek as the water supply. Water is siphoned from the Creek via an infiltration gallery under the creek bottom. In 2000, to reduce turbidity problems during very high and low flows, the infiltration gallery was moved upstream and buried further underground. In 2009, the District constructed a 100,000 gallon steel water tank with the assistance of Proposition 50 Integrated Regional Water Management Plan Implementation Grant, to increase water supply reliability, fire protection, emergency water supply and maintenance of bypass flows in Wages Creek as required by the water right. The tank is located above the community and provides water supply via gravity. Although it provides improved water supply reliability within the District, the tank provides limited term storage (10 days, up to 30 days with conservation measures implemented) and water rationing has been implemented during times of high turbidity. Additionally, the District has a 100,000 gallon Redwood Water Tank. The Redwood Water tank is in a state of degradation and is leaking. Staff has identified two solution alternatives: line the tank; or repair the floor of the tank. The District currently has no funding for completing either alternative and continues to monitor and temporarily patch the leaks as best it can.Water storage needs also include fire storage, which is required to meet standards of 1,500 GPM flow for 2 hours. This flow and duration corresponds to a fire storage volume of 180,000 gallons, nearly all of the District’s current storage capacity. Additionally, emergency storage is needed to ensure water service is continued in the event there is an interruption in water supply, a transmission line breaks, or if there are other emergency needs. Emergency storage is typically one to three days of existing water demand, which was estimated at nearly 80,000. The District’s distribution consists of two water storage tanks, a waterline network, meters, and a fire hydrant system. The hydrant system is up to date. Transmission lines consist of a four-inch PVC pipe that conveys water from the District’s treatment plant along Wages Creek to the road leading up to the storage tank. ( Refer to Figure 9-9: Water Transmission System) From there a six -inch PVC pipe connects the storage tank with the distribution system. The remainder of the distribution system is composed primarily of six-inch pipe constructed of asbestos-cement, PVC, and ductile iron. The lines remain in serviceable condition; however the mains are more than 35 years old and are reaching the end of their useful lives. The distribution lines are fed from the storage tanks, which are co-located thereby essentially feeding the distribution lines from one source. It is unknown whether or not the District has a capital improvement plan in place to plan ahead for replacement of aging distribution and transmission lines. | Fair condition/ Upgrades planned/ identified | The District drilled a deep well, which has a high flow rate, but is unusable because of high manganese and iron content. Use of the well water requires a filtration system that had a 2001 estimate of more than $100,000. There is currently no funding for construction of a filtration system. | 0 | 1. Total coliform monitoring violation 2. Bacteriological monitoring and reporting violation | 1. 7/17/2017 2. 9/19/14 |  |  |  |  | The WCWD provides wastewater services to 66 residences and has treatment capacity of a maximum of 20,000 GPD per day averaged over a period of 30 consecutive days. The Westport Wastewater Treatment Plant is designed to provide secondary treatment for up to 20,000 gallons of wastewater per day of average dry weather flow. Treatment consists of two aerated ponds followed by an 11.3 MG polishing/storage pond. Wastewater from the polishing/storage pond is disinfected prior to being irrigated over a 16.8-acre open field west of the community. Solids are reduced to an insignificant volume in the aerated ponds. The Plant also handles approximately 6.4 million gallons of rainfall and stormwater annually. A Grand Jury Report in 2001-2002 identified the sewage settlement ponds as suffering from sediment accumulation and sewage seepage. The District has no funds available for the required dredging, draining, and lining. IRWM funding received. | Adequate
|  | 1 | Wildwood Campground | other | 29700 Highway 20 FORT BRAGG,CA 95437 |  |  |  | 50 | [24 empty] | Mendocino | North Coast, Region 1 | 48563 | n | 150 | GW | Wells (3)
| y | 1 | WILDWOOD RETREAT (WILDWOOD CONSERVATION FOUNDATION) | other |  | y | y |  | 0-25 | In house systems, no charges | Unfamiliar; interested | [19 empty] | 1 |  | Staff and guests of the retreat center in Sonoma County | Sonoma | North Coast, Region 1 | 45489 | n | 50-100 | [7 empty] | An onsite well would be great, currently we buy our water from a neighbor with a well. | Adequate | [7 empty] | septic | single septic system | Adequate
|  | 1 | Willits City WWTP | City | 300 North Lenore Street, Willits, CA 95490 | [28 empty] | Mendocino | North Coast, Region 1 | 32667 | n | [14 empty] | C | 1. Water Quality Certification for the Willits Emergency Waterline Replacement Well 2. Water Quality Certification for the Willits groundwater test well project 3. NOV and Transmittal of 3/13 Compliance Evaluation Inspection Report. Deficiencies include: laboratory deficiencies; late Biosolids Report; lack of documentation of calibration; time-paced rather than flow based influent and effluent composite samplers; foaming at discharge point 003. | 1. 3/4/15 2. 6/21/17 3. 4/24/13 |  | The City owns, operates, and maintains a public wastewater system includingwastewater collection infrastructure, the recently upgraded Wastewater Treatment Plant (WWTP), and water reclamation facilities. | Adequate
y |  | 1 | WILLITS, CITY OF | City | 111 EAST COMMERCIAL WILLITS, CA 95490 | y | y | y | 2415 | Monthly/ annual flat rate | Familiar; infrequent participation | Funded | [12 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | Willits, CA | Mendocino | North Coast, Region 1 | 32667 | n | 6175 | SW | IN - Morris Reservoir |  |  | 51-100 | $51 - $100 | completely upgraded the Water Treatment Plant in 2015, added a third filter and a 220,000-gallon pre-treatment upflow solids contact clarifier, lined the 3MG main water storage tank in 2016, and replaced 3,400-feetof 10-inchsteel pipe with 12-inchductile iron and C-900pipingin 2009 and 2016(Willits, Nov 2018). | The City owns, operates,and maintains a public water system including water supply facilities, a Water Treatment Plant (WTP), and distribution infrastructure. The City’s water system is classified as a Large Water System because it has more than 500 connections and is under the jurisdiction of the State Water Resources Control Board (SWRCB) Division of Drinking Water.The City’s Water Department is responsible for the water enterprise service. Through an agreement executedin November of 1995, the City provides water and wastewater services to the Sherwood Valley Band of Pomo Indians Rancheria located southwest of the City limits,which includes residential units, a community center, and the Sherwood Valley Casino. This agreement provides for the water needs of up to 50 residential units or their functional equivalent.(LAFCo, 2015)The City’s water supply is a combination of surface water from Davis Creek and groundwater from the Elias Replacement Well. Davis Creek is a tributary to Outlet Creek,which is tributary to the Eel River. The City stores water along Davis Creek at Morris Reservoir with 726 acre-feet(AF) capacity and Centennial Reservoir with 635 AF capacity. The watershed area for Davis Creek upstream from MorrisDam is 4.9square miles (3,136 acres).(LAFCo, 2015; Willits, Nov 2018)The City’s WTP is located adjacent to Morris Dam, has a capacity of 3.3 million gallons per day (MGD),and utilizes alternative filtration technology and an upflow clarifier process to produce treated water.The City has five water storage tanks, with a total capacity of 4.711 million gallons (MG),including: a 3.0 MG tank installed in 1980,a 1.5 MG tank and clear well installed in 1989 (both adjacent to the treatment plant),a 0.125 MG tank on Locust Street installed in 1993,a 0.043 MG tank on Laurel Street installed in 1977,and a 0.043 MG tank on Berry Hill installed in 1980. There are eight pressure zones within the City’s water distribution system.(LAFCo, 2015)The City has taken the following corrective actions to meet drinking water standards: completely upgraded the Water Treatment Plant in 2015, added a third filter and a 220,000-gallon pre-treatment upflow solids contact clarifier, lined the 3MG main water storage tank in 2016, and replaced 3,400-feetof 10-inchsteel pipe with 12-inchductile iron and C-900 pipingin 2009 and 2016(Willits, Nov 2018). On October 17, 2014, the SWRCB issued the City a compliance order which determined that the City did not have a reliable supply of water to serve its customers due to the drought conditions and senior water right demands. The order allowed the City to serve existing customers, but prohibited new service connections. It also required the City to secure a reliable long-term supply of water. This order by the SWRCB was rescinded at the end of November 2014 based on further information provided by City Staff to the SWRCB that addressed theirconcerns.(LAFCo, 2015)On August 9, 2017, the City Council approvedfull-time use of the Elias Replacement Well to supplement the City's surface water supply.Groundwater is now a regular water supply to the City’s water system, instead of being limited toemergency situations.A Source Capacity Analysisprepared for the City by GHD consultants specified a maximum well capacity of 800 gallons per minute (gpm); however, with head-loss, friction, and overcoming system pressure, the well pump is a limiting factor. The City routinely pumps this groundwater well at aproduction rate of 330 gpm and proposes not to exceed a total annual use of 400 AF (131MG).The City is currently evaluating potential enhancements to this groundwater system including changing the configuration and increasing the pump size. The Elias Replacement Welloffers a consistent high quality water source that is not prone to seasonal water quality issues like surface water sources. (Willits, 2017b; Willits, Nov 2018). | Fair condition/ Upgrades planned/ identified |  | C | 1. Exceeded MCL for disinfection byproducts in 2015 2. Failure to comply with MCL for a disinfection byproduct | 1. 8/12/2015 2. 10/8/13 |  |  |  | sewer | The City’s WWTP is located in the northeast corner of the City at the end of Sewer Plant Road via North Lenore Avenue and East Commercial Street and the northerly portion of the treatment plant area is located outside the City limits. The City’s wastewater system includes a sewage collection system consisting of approximately 22-miles of gravity-fedsewer mains ranging in size from 4-inches in diameter to 24-inches in diameterand one lift station and 450 manholes. The WWTP also includes associated reclamation and disposal facilities.From October 1 through May 14, treated wastewater is discharged from Discharge Point 003 to Outlet Creek, downstream of the confluence of Broaddus Creek and Baechtel Creek, consistent with the City’s NPDES permit #CA0023060 from the North Coast Regional Water Quality Control Board (RWQCB), and from May 15 through September,and all other times seasonally appropriate, treated wastewater is recycled via irrigation on adjacent pasture lands (Willits, 2019). | Adequate | Major flood areas include low-lying lands east of Willits.
y |  | 1 | WILLOW COUNTY WATER DISTRICT | Water Dist | 151 LAWS AVENUE UKIAH, CA 95482 | y | n | y | 1070 | uniform rate schedule | Familiar; infrequent participation | Unfunded | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2,760 acres immediately south of Ukiah | Mendocino | North Coast, Region 1 | 19356 | n | 4200 | GW | Wells (5) |  |  | 51-100 | $51 - $100 |  | The WCWD maintains a storage capacity of 1.348 million gallons in nine storage tanks strategically located throughout the WCWD. It has surface water rights of 2,166 AF and can purchase up to 515 AF from Russian River Flood Control District. Demand in 2010 was 1,301 AF and is expected to increase to 1,904 AF in 2030, assuming there are no conservation measures in place. Total supply from all sources is estimated at 2,681 AF in a normal year and 2,308 AF in an extended dry year. The WCWD supplies water through a number of sources, including wells, surface water, and Lake Mendocino water. The WCWD has surface water rights for 1,440 AFY from November to June and 726 AFY year round through diversion of underflow of the Russian River. The WCWD also contracts with RRFC for 515 AFY. The WCWD has five wells, of which three are used only during dry months. The total capacity of the two well fields is 2,700 gallons per minute. The WCWD does not operate a treatment plant. Domestic water is treated in the pump house at the well site. In addition, there are nine storage tanks with a capacity of 1,348,000 gallons. The WCWD has signed a contract to replace the 100,000-gallon storage tank at Firecrest 1 with a 350,000-gallon tank. When that work is complete, the WCWD will have a storage capacity of 1.598 million gallons. The WCWD works with other water agencies in the Ukiah Valley and maintains an emergency intertie with the City of Ukiah. Cooperation among the water agencies is facilitated by the fact that RRFC, Millview, Calpella, Hopland, Ukiah Valley Sanitation District, and Willow all have offices in the 151 Laws Avenue building. The Ukiah Valley Special Districts Municipal Service Review of 2013 recommended that Willow CWD, Calpella CWD, and Hopland PUD consider a formal consolidations through LAFCO. | Good condition | [11 empty] | 1
y | y | 1 | WILLOW CREEK C.S.D. | CSD | P O BOX 8 WILLOW CREEK, CA 95573 | y | y | n | 912 | monthly/ annual flat rate,;uniform rate schedule | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | Willow Creek, CA | Humboldt | North Coast, Region 1 | 32209 | n | 1710 | GU | Wells (5) |  |  | 0-50; we have high bills in the summer when persons are using lots of water for irrigation of lawns, gardens and cannabis. | $0 - $50 | The water is chlorinated and treated before it placed into the distribution system. The District monitors chlorination and turbidity 24 hours a day. | The District source of supply is from Willow Creek. It consists of six wells located in the mouth of Willow Creek. Four wells draw water from infiltration galleries in the Willow Creek flood plain acting as a natural filtration system. The District has a pumping capacity of 1.9 million gallons per day. The daily average consumption during peak time is 1.6 million gallons per day. Water storage capacity is 1.1 million gallons. The District’s source of supply consists of six wells located in the mouth of Willow Creek. The Willow Creek CSD operates six production wells. Four wells draw water from infiltration galleries in the Willow Creek, which are believed to be under the influence of surface water, and two wells separate from the infiltration gallery, which may or may not be under the influence of surface water. A new water treatment plant was completed in 2007, and has a design capacity of 2,140 gpm. If run for 23 hours per day, treatment capacity is approximately 2.953 MGD. Total source capacity is 2,610 gpm, or 3.76 MGD. Willow Creek CSD’s water system is generally in good condition, although per capita demand is very high (1,861 gpd/cap) and may be the result of system leaks. Current peak water use is approximately 48% of available production capacity. The new water treatment plant has been designed for 2,140 gpm, approximately 40% greater than existing peak day demands. The District does not have adequate storage capacity and has plans to construct of a new 400,000 gallon storage tank above the new treatment plant and Brannan Mountain Road. | Fair condition/ Upgrades planned/ identified | [8 empty] | Willow Creek has been evaluating alternatives for a community wastewater system for a number of years. Willow Creek’s business center along Highway 299 is in need of a centralized wastewater system due to existing disposal field problems which currently limit development. A preliminary engineering report was prepared for the system in 2008 and additional alternatives are under consideration. The ultimate type, location, and construction schedule for a Willow Creek wastewater treatment plant is dependent upon future funding availability and NCRWQCB permitting requirements. The Willow Creek CSD received a Planning/ Preliminary Design Grant for a community wastewater system for the downtown area of Willow Creek. This grant will allow the community of Willow Creek to determine if a wastewater system is a possibility for the downtown area and help determine more detailed estimated costs. A Draft Environmental Impact Report for the Willow Creek Community Services District Downtown Wastewater Development Project was prepared in June, 2015 (SCH #2015012014) and a Final EIR was certified by the District in September, 2015. | Fair condition/ Upgrades planned/ identified
|  | 1 | WILLOWSIDE MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 42958 | n | 350 | GW | Wells (2)
|  | 1 | WILSHIRE HEIGHTS MUTUAL WATER COMPANY | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | 46037 | n | [11 empty] | A | 1. MCL Violation for total coliform for December 2016 2. same | 1. 3/7/2017 2. 1/31/17
y |  | 1 | WINDSOR, TOWN OF | City | P.O. BOX 100 WINDSOR, CA 95492 |  |  |  | 8883 |  | Familiar; infrequent participation | Unfunded | [20 empty] | Town of Windsor, Airport Industrial Park and Sonoma County Airport, Mayacama and Shiloh Estates | Sonoma | North Coast, Region 1 | 39614 | n | 27183 | GW | Purchased, Wells (5) |  |  |  |  | Windsor's water supply is naturally high quality. As a result, only chlorine disinfection is required to meet drinking water standards. The pH of the water is adjusted to protect the Town distribution and home plumbing systems from the natural effects of corrosion. | [6 empty] | 0 | 1. Failure to submit 2015 - 2016 Annual Report as required by General Permit for Storm Water Discharges Associated with Industrial Activities, Windsor Wastewater Treatment Plant, WDOD No. 1 49I020487 | 1. 8/4/2016
y |  | 1 | Woods, The (Mendocino) | Other |  | y | y | y | 109 | Don't charge for water, have sewage fee for each home, standard monthly fee. | Unfamiliar; interested |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | Little River, CA | Mendocino | North Coast, Region 1 | 39667 | n | 150 | GW | Well |  |  | 57 | $51 - $100 | [10 empty] | sewer
y | y | 1 | WOODSIDE RV PARK & CAMPGROUND | other | 17900 N. HWY 1, FORT BRAGG, CA 95437 | y | n | y | 57 | Trailer park residents are not metered...water use included in space rental. |  |  | 1 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | Woodside RV Park 17900 N Hi. 1 Ft Bragg CA 95437 | Mendocino | North Coast, Region 1 | 31027 | n | 280 | GW | Wells (5) |  |  | Water and Sewer are included as part of the Monthly Rental rate Per Space. There is currently no breakdowns for what portion of the Monthly rate is for those utilities.
y | y | 1 | YREKA, CITY OF | City | 856 N. MAIN STREET YREKA, CA 96097 | y | y | y | 2993 | flat rate based on meter size with variable usage rates | Unfamiliar; interested |  | 1 | 3 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 |  | Yreka, CA | Siskiyou | North Coast, Region 1 | 25493 | n | 7290 | SW | IN - Fall Creek Intake Dam A, Well, raw, standby |  |  | 0-50; ~$48 for water alone | $0 - $50 | Water from Fall Creek is chlorinated and filtered before it is delivered to ourcustomers. All water systems using surface water are required to routinely measure the turbidity or "clarity" of the filtered water. Turbidity measurements are needed in order to monitor the effectiveness of the filtration process at removing microbiological contaminants that may be found in surface water. | [6 empty] | D | 1. Notice of Violation of SWRCB General Permit for Storm Water Discharges from Small Municipal Separate Storm Sewer Systems | 2016-07-25 | sewer
y | y | 1 | YULUPA MUTUAL WATER COMPANY | Mutual | P.O. Box 2513 SANTA ROSA, CA 95405 | n | y | y | 59 | monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 0 | 3 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | Woodside development in rural Sonoma County, | Sonoma | North Coast, Region 1 | 46037 | n | 200 | GW | wells (3) |  |  | 100-150 | $101 - $150 |  |  |  | Iron and manganese. | [10 empty] | 1
|  | 308 | [55 empty] | Totals | 16 | 6 | 6

## DAC & "C" Comm Needs Table
Agency Characteristics | [35 empty] | Community Characteristics |  |  |  |  | Drinking Water | [9 empty] | Regulatory Issues | [5 empty] | Wastewater |  |  | Stormwater |  | Affordability
2017/18 Survey Response | 2014 Survey Response | Water/ Wastewater System | Median Household Income (MHI) | DAC | SDAC | EDA |  |  | System has paid FT staff (y/n) | System has identified itself as in need of financial assistance (y/n) | System has a current Emergency Response Plan (y/n) | # Hookups | Rate structure | Involvement with NCRP | Has Submitted Project to NCRP | Level of concern for system on the following topics (0 = no concern, 1 = moderate, 2 = strong, 3 = extreme, N/A = N/A "blank" = no response): | [11 empty] | Level of need for technical assistance (0 = no concern, 1 = moderate, 2 = strong, 3 = extreme, N/A = N/A "blank" = no response): | [16 empty] | Average Monthly Bill (either water, wastewater, or both) | [16 empty] | EPA Affordability Criteria Threshold
|  |  |  | $38,270 < MHI < $51,026 | MHI< $38,270 | $51,026 < MHI < $54,216 | Type | Address | [7 empty] | Water Quality - raw | Drinking water supply reliability | Fire suppression supply reliability | Water pressure issues | Outdated treatment system | Aging treatment system | Sufficient quality and quantity of staff | System too small; population increasing | System too large; population decreasing | Financial stability for operating system and maintaining reserve | Operation and maintenance – need for trained personnel | Meeting current regulations | System infrastructure - operations | System infrastructure - maintenance and repair | Equipment calibration | Administration | Capital Improvement Planning | Rate Structures | Funding Opportunities | Meeting Current Regulations | Community | County | IRWM region | Tribal Community (y/n) | Population | Primary source of water | Specifics about water source(s) | Estimate number of private wells | Estimate number of public wells |  | Monthly Bill Categories | Water Treatment Information | Drinking water system issues & system status | Drinking Water System Status Categories | Anything (other than AS) unusual or problematic about water source? | DDW Rank | DDW Violation Type | DDW Action Date | SWRCB Rank | RWQCB Decision Type | RWQCB Date | Type of system | Describe any insufficient wastewater system issues & system status | Sewer System Issue Categories | Identify stormwater/ urban water runoff/ flood management issues | Water > 2.5% | WW > 2% | Both > 4.5%
y |  | ALBION MUTUAL WATER COMPANY | 39667 | 1 |  |  | Mutual | PO Box 485, Albion, CA 95410 | n | y | y | 27 | seasonal | Unfamiliar; interested |  | 1 | 1 | 2 | 0 | 0 | 2 | n/a | n/a | n/a | 1 | N/A | 0 | 1 | 0 | 0 | 1 | 0 |  | 2 |  | Albion Village | Mendocino | North Coast, Region 1 | n | 40 | GW | Wells (2) |  | 2 | Average service fees range between $41 and $60 per month. | $51 - $100 |  | The Company has two active wells (East and West Wells) and owns and/or maintains approximately 0.8 miles of pipeline and no additional infrastructure. | Good condition | no
| y | ALDERPOINT COUNTY WATER | 26813 |  | 1 |  | Water Dist | P.O. Box 117 ALDERPOINT, CA 95511 | n | y |  | 79 | uniform rate schedule | Familiar; infrequent participation | Unfunded | [13 empty] | 1 |  | 1 | 1 |  | 1 |  | Alderpoint | Humboldt | North Coast, Region 1 | n | 219 | SW | IN - Eel River - untreated |  |  | 0-50; minimum monthly fee of $40.00 for first 2,000. cu. ft. after that additional usage will be billed according to use at same rate per cubic foot. | $0 - $50 | Calcium hypochlorite, a disinfectant, is added to the water in the 5,000-gallon tank. From the 5,000-gallon staging/preliminary distribution tank, water is pumped up another 300-feet, via a six inch main, to a 100,000-gallon redwood storage tank. This main storage tank feeds water into the distribution system serving the community. The source of water for the District is an infiltration gallery in the Eel River bed. The infiltration gallery collection pipe is approximately nine feet below the bed of the river. From the infiltration gallery wet well, water is pumped through a six-inch cast iron main to a 5,000-gallon staging tank located 130 feet above the riverbed. The 5,000-gallon tank and its accompanying pump house are located just off River Road. Calcium hypochlorite, a disinfectant, is added to the water in the 5,000-gallon tank. From the 5,000-gallon staging/preliminary distribution tank, water is pumped up another 300-feet, via a six inch main, to a 100,000-gallon redwood storage tank. This main storage tank feeds water into the distribution system serving the community. The Alderpoint CWD recently installed a water filtration system to bring the water quality into compliance with State of California regulations. In 2014, Alderpoint CWD replaced a leaking 100,000-gallon redwood tank with a new 160,000-gallon steel tank, which reduced the amount of water withdrawn from the Eel River by at least 50 percent. |  |  | no | A | 1. Violation of MCL for total coliform bacteria 2. Failure to submit monthly monitoring reports 3. Violation of Section 116555 pf the CA Health and Safety Code, which requires each public water system to have a reliable supply of water to serve its customers | 1. 4/26/2017 2. 10/8/15 3. 10/17/14
|  | Anderson Valley Community Services District | 36932 |  | 1 | [31 empty] | Mendocino | North Coast, Region 1 | n | 1035 |  |  | > 23 |  |  |  |  | We are currently in the planning process which consists of a feasibility study that establishes a proposed service area, identifies options to develop public utility service (water or wastewater) within it, evaluates the options with respect to cost, environmental impacts and acceptability to the community, and concludes with a recommended project description. The recommended project will then be presented to the community for comment and, after receipt of public input, modified as directed by the District. Based on community support, the District will then determine whether to move forward to seek financing for implementation of the project including proceeding with the establishment of local mechanisms (rates, assessments, etc.) that would ultimately be needed to repay possible project loans and fund system operations and maintenance. Phone call with Joyce Andrews (General Manager), 1.9.20: proposal to build wwtp and water supply facilities will be presented to rate payers for decision mid-2020. The water proposal is moving forward well - the district is in discussion with several property owners with good water quality and flow to their wells to construct many small wells that will feed into a few treatment facilities. A recent fire in Boonville underscored the need for fire suppression capability - the new water system will be required to include fire suppression tanks. There is more resistance to the wastewater treatment plant with respect to siting. Although it will use MBR technology, which is odorless, soil percolation and neighbor (NIMBY) constraints are making it difficult to find a site. Within the next several months, the district will decide whether to separate the projects and if they do, they will need to redo CEQA. Projects are expected to be fully funded through the state. | Fair condition/ Upgrades planned | [7 empty] | septic | There is historical evidence of private well contamination in Boonville that is most likely attributable to the proximity of wells and onsite septic systems. The presence of small lots in portions of the community exacerbate the problem. Also, many septic systems are nearing the end of their useful life and in some circumstances there is insufficient space for a standard replacement leach field. When a system fails, the only viable alternatives are in these circumstances very expensive. In 2016, water quality testing of samples drawn from 23 wells in the densest housing areas revealed alarming levels of E Coli and nitrates confirming a health issue exists. Funding is currently available under State Proposition 1 to create municipal utility systems. This is a relatively new program and this is an opportunity to take advantage of it. The District is interested in developing utility systems under Proposition 1 programs that provide for planning grants to eligible communities to help make projects affordable. | Regulatory - septic
|  | ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | 45489 | 1 |  |  | Public Utility | 1720 NORTH FIRST STREET SAN JOSE, CA 95112 |  |  |  | 377 | [24 empty] | Sonoma | North Coast, Region 1 | n | 420 | GW | Wells (2) |  | 2
|  | ATHENA TERRACE MUTUAL WATER COMPANY | 46037 | 1 |  |  | Other | Sonoma County | [28 empty] | Sonoma County |  | n
|  | Austin Creek Mutual (Springhill) | 41389 | 1 |  |  | Mutual | P.O. BOX 86 CAZADERO,CA 95421 |  |  |  | 63 | [24 empty] | Sonoma | North Coast, Region 1 | n | 150 | GU | Wells (2) |  | 2
|  | BEACH CREEK MH PARK | 20346 |  | 1 |  | other | 3633 Patricks Point Dr, Trinidad, CA 95570 4203 Lowell Ave., La Crescenta, CA 91214 | [28 empty] | Humboldt | North Coast, Region 1 | n
|  | BENBOW W.C. | 36371 |  | 1 |  | Public Utility | Public Utility |  |  |  | 135 | [24 empty] | Humboldt | North Coast, Region 1 | n | 150 | SW | IN- East Branch, South Fork Eel | [5 empty] | The Benbow Water Company diverts water from the East Branch of South Fork Eel River through an infiltration gallery located within the river bed. The Benbow Water Company produced approximately 31 million gallons of drinking water in 2005 (2006 California Department of Public Health, now the State Water Resources Control Board Division of Drinking Water (DDW), Annual Inspection Report). Source capacity was identified as a serious problem for this system and pumping capacity was less than maximum day capacity (Winzler and Kelly, 2008, Page 6-91). The Benbow Water Company completed a project to increase filter capacity by installing an additional filter bank. The original filters had a surface area of 39 sq. ft., and were increased to a total surface area of 78 sq. ft. (Personal communication, Troy Hubner, Del Oro Water Company, February 8, 2017). The Benbow Water Company reports that it is operating at approximately 40 percent of its claimed water right (Personal Communication, Winston Benbow, 2010), and is planning to accommodate an additional 20 to 50 new water connections in the next 20 years. | Uncertain water supply |  | 0 | 1. Failure to Monitor for coliform. | 1. 3/7/2013
|  | BENNETT RIDGE MUTUAL WATER COMPANY | 46037 | 1 |  |  | Mutual | Sonoma County | [28 empty] | Sonoma County |  | n
| y | BERTSCH OCEANVIEW CSD | 26544 |  | 1 |  | CSD | 377 J STREET CRESCENT CITY, CA 95531 | n | n |  | 629 | They contract with Crescent City, which sells water to individuals, and the Bertsch Oceanview CSD charges a water service fee on top of that, for maintenance of the system. | Familiar; not a participant | [21 empty] | Some unincorporated areas of Del Norte County. | Del Norte | North Coast, Region 1 | n | 1600 | GWP | CC Smith River Purchased Water - treated XCLD |  |  | $0-50; Bertsch Ocreanview's monthly service fee: $9.75. They contract with Crescent City, which sells water for a minimum monthly cost of $12.30 for 0-500 cubic feet, plus $1.07 for each additional cubic foot. | $0 - $50 |  | The BOV CSD receives its water from the City of Crescent City. From the City’s distribution center, water is conveyed south, through a 12-inch diameter BOVCSD waterline, until it reaches a booster station located on Elk Valley Road.The booster station contains two pumps with sufficient generator backup power for simultaneous operation. Each pump can deliver approximately 550 gallons per minute (GPM) and together, approximately 900 GPM. Typically, a single pump is operated daily for 7-9 hours (depending on the season). The backup power generator has enough electrical capacity and fuel to continuously operate both pumps for a minimum of 24 hours. The distribution system that is upstream of the booster station is considered the BOVCSD water distribution system. The District notes that there are a few BOVCSD connections located downstream of the booster station as well. The BOV CSDwater distribution system contains approximately 12.8 miles of 4-inch-12-inch piping, the majority of which (74%)is 6-inches and 8-inches in diameter. The majority of the BOVCSD’s existing water distribution system was constructed in 1973 and is predominately Asbestos Cement Pipe.The District maintains a 750,000 gallon reservoir that was constructed in 1998. In general, the BOV CSD’s water distribution system has few known deficiencies. The BOV CSDmaintains a master water meter within the booster station and the volume is recorded by Crescent City personnel on a daily basis. The following calculations for the maximum daily demand (MDD) were based on the highest “normalized” data readings. The 2008 normalized MDD was 418,000 gallons. Of the District’s 750,000 gallon reservoircapacity, 300,000 gallons are maintained for fire flows. The remaining 450,000 gallons are available for the District’s useto deliver to its customers. The District reports that there is sufficient capacity within the existing reservoir to maintain the MDD of the BOVCSD without having to utilize the booster station’s available pumping capacity | Good condition
y | y | BIG LAGOON CSD | 50417 | 1 |  |  | CSD | P.O. Box 847 TRINIDAD, CA 95570 | y | n | y | 40 | monthly, annual flat rate | Familiar; infrequent participation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | Big Lagoon | Humboldt | North Coast, Region 1 | n | 109 | GW | Wells (2) |  | 2 | 51-100 | $51 - $100 |  | The water system now consists of 2 wells, a 20,000 gallon redwood storage tank, booster pumps and 3,000 gallon hydro pneumatic tank with an air compressor. In 2016, the Chairperson of the CSD Board reported that the system has an “untested theoretical limit of 30,000 gallons per day, if the well runs constantly. This is different from the 70,000 gallons reported (by the Community Infrastructure and Services Technical Report).” (Personal Communication with Valen Castellano, Big Lagoon CSD, April 29, 2016). The system operates with only 10,000 gallons of storage. The Chairperson further stated, “The BLCSD has discussed more water storage, but we are a long way away from realizing the project. Many believe we are at capacity now and could only service one or at most, two new connections. We will review and consider each individual proposal on its particular merits. Further development inland would require serious study and possible expansion of our service area beyond our current 23 acres. An Engineering Study must be done on our current system before we could competently evaluate our current conditions and any room for expanding services.” (Personal Communication with Valen Castellano, Big Lagoon CSD, April 29, 2016) | Uncertain water supply | [7 empty] | sewer
y | y | BIG LAGOON PARK WATER CO. | 20346 |  | 1 |  | other | P.O. BOX 654 EUREKA, CA 95501 | y | n | y | 76 | monthly/ annual flat rate | Unfamiliar; disinterested |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | Big Lagoon Park | Humboldt | North Coast, Region 1 | n | 70 | GW | Wells (2) |  | 2 | 0-50 | $0 - $50
|  | BIG RIVER VISTA MUTUAL WATER COMPANY | 51277 |  |  | 1 | Mutual | PO Box 708, Mendocino, CA 95460 | n |  |  | 19 |  | Unfamiliar; disinterested | [21 empty] | Big River area near Mendocino, CA | Mendocino | North Coast, Region 1 | n | 36 | GW | Well |  | 1 | Average service fees range between $81 and $100 per month. | $51 - $100 |  | The Company owns and maintains one active well and approximately two miles of pipeline. In addition, the Company owns a well pump, water storage tank and pump, tank liner, treatment building, water treatment equipment, distribution valves, customer meters, and three standpipe hydrants. | Good condition
y | y | BIG ROCK C.S.D. | 26544 |  | 1 |  | CSD | P.O. BOX 453 CRESCENT CITY, CA 95531 | y | y | y | 107 | Increasing block (graduated) rate schedule | Familiar; regular participant |  | 0 | 3 | 0 | 0 | 3 | 3 | 1 | 0 | 0 | 3 | 1 | 0 | 3 | 3 | 1 | 0 | 2 | 3 | 3 |  | Township of Hiouchi | Del Norte | North Coast, Region 1 | n | 400 | GW | Well |  | 1 | 51-100 | $51 - $100 |  | The Big Rock CSD collects its water from a single well located adjacent to the Smith River. The District’s total storage capacity is 150,000 gallons, including one 100,000-gallon Redwood tank and one 50,000-gallon Redwood tank. The Big Rock CSD replaced its two submersed river pumps in October 2008 and was reclassified as a groundwater system. Because the pumps’ operating schedules are alternated, they should not have to be replaced for another 13 years. In July 2009, the Big Rock CSD added a newer small pump at the large storage tank (used to push water further uphill into the 50,000-gallon tank) due to the existing primary pump’s mature age. (LAFCO 2015) | Adequate | [7 empty] | septic |  |  |  | 1
y | y | BLUE LAKE, CITY OF | 49828 | 1 |  |  | City | P.O. BOX 458 BLUE LAKE, CA 95525 | y | y | y | 699 | monthly/ annual flate rate | Familiar; infrequent participation | Unfunded | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 2 | 1 | 2 |  | Blue Lake, CA | Humboldt | North Coast, Region 1 | n | 1252 | GWP | Purchases treated from HBMWD |  |  | 51-100 | $51 - $100 | We don't treat; we provide pre-treated water to our customers. | The City’s receives its water supply through contract with HBMWD. Water is delivered through distribution mains and storage reservoirs located throughout the community. The City has approximately 0.9 MG of storage capacity spread over two redwood tanks ranging in size from 400,000 gallons to 500,000 gallons. | Adequate | [8 empty] | The Glendale area receives wastewater service from the Fieldbrook-Glendale CSD. Glendale’s wastewater system is in very good condition overall and has approximately 166 connections. Flows currently range between 37,000 gpd during dry weather and 75,000 gpd during wet weather. The District has a contract to pump raw wastewater to the City of Arcata for treatment and disposal. The existing contract allows for up to 71,200 gpd average dry weather flow, indicating that the system has the capacity for approximately 80 to 100 more connections. Alternative solutions to treatment and disposal must be found toaccommodate any development in excess of this. The City of Arcata has indicated it is not interested at this time in increasing the District’s contract amount and has recommended the District consider other alternatives. The District has approached the City of Blue Lake and will participate in other related studies to evaluate alternatives and costs for potential interconnection. | Good condition
|  | BRAND WATER COMPANY | 46037 | 1 |  |  | Other | Sonoma County | [28 empty] | Sonoma |  | n
|  | BRANGER MUTUAL WATER COMPANY, INC. | 46037 | 1 |  |  | Other | Sonoma County | [28 empty] | Sonoma |  | n
|  | Branscomb Mutual Water Company | 32667 |  | 1 |  |  | 13270 Kenny Creek Road, Branscomb, CA 95417 P.O. BOX 72 BRANSCOMB BRANSCOMB, CA 95417 | n |  |  | 23 | [23 empty] | Branscomb | Mendocino | North Coast, Region 1 | n | 92 | SW | IN - GP Spring - Surface water |  |  | Average service fees range between $61 and $80 per month. | $51 - $100 |  |  |  | The Safe Drinking Water Information System lists a number of monitoring violations, dated as recently as September 2017 with compliance achieved March 11, 2018. The United States Environmental Protection Agency (USEPA) notes a monitoring and reporting violation dated January 2009 with compliance achieved in April 2010.6 | 0 | 1. Bacteriological monitoring violation 2. Chemical monitoring violation 3. Citation for NonCompliance | 1. 9/11/17 2. 11/30/17 3. 8/31 17
y |  | BRICELAND C.S.D. | 37778 |  | 1 |  | CSD | P.O. Box 670 REDWAY, CA 95560 | n | y | y | 26 | monthly/ annual flat rate | Familiar; infrequent participation | Funded | 0 | 2 | 2 | 0 | 0 | 3 | 1 | 3 | 0 | 3 | 1 | 0 | 2 | 2 | 0 | 0 | 1 | 1 | 1 |  | Briceland | Humboldt | North Coast, Region 1 | n | [5 empty] | 0-50 | $0 - $50 | The Briceland CSD anticipates installing a new roughing filter and a solar powered hypo chlorination unit in the near future. | high rainfall turbidity; The District currently serves 26 lots in the District and 1 outside District boundaries. District representatives have indicated that: “Due to regulatory constraints, the District has no plans of expansion either in terms of size or number of service connections. There are presently four applications for service, the oldest of which has been held on file for more that ten years. The District was formed for the purposes of improving the water system that was supplying water to houses in the Briceland area. The water system that was in place at the time was an antiquated system put in by the original settlers in the 1880’s. The Briceland CSD water system is in poor condition, source capacity is unable to meet current maximum day demands, the treatment system is unable to meet turbidity performance standards during winter months, and storage capacity is barely able to meet even one day of maximum day demands. Briceland is currently operating under a moratorium for new connections. There are currently at least four homes within the District that have submitted requests for service connections; the oldest request is over 16 years old. The Briceland CSD anticipates installing a new roughing filter and a solar powered hypo chlorination unit in the near future. | Poor condition | [7 empty] | septic
| y | BROOKTRAILS TOWNSHIP CSD | 32667 |  | 1 |  | CSD | 3800 Chinquapin Drive WILLITS, CA 95490 |  |  |  | 1554 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Mendocino | North Coast, Region 1 | n | 3800 | SW | Instream | [5 empty] | The Districtowns, operates, and maintains a public water system forwater supply, treatment, and distribution. The District’s water system facilities and infrastructure includes two reservoirs, Lake Emily which feeds into Lake Ada Rose,on Willits Creek and a tributary within the Eel River watershed, aWater Treatment Plant (WTP) with adesign capacity of 1.2 million gallons per day (MGD), 24 water tanks with 1.7 million gallons(MG)of storage capacity, 18 pump stations, and 64 miles ofwater mains. The District also has a four-bay utility department garage located at the WTP.The District’s water system is classified as a Large Water System because it has more than 500 connections and is under the jurisdiction of the State Water Resources Control Board (SWRCB) Division of Drinking Water Supply Permit No. CA2310009.The District’s water system serves a total of 1,555 connections, including 1,505 in Brooktrails Township, 49 connections in Spring Creek, and 1 connection to the City of Willits for the Willits Municipal Airport.The District’s water system serves 1,548 residential, 4 commercial, and 3 public service connections.Lake Emily has a physical storage capacity of 251acre-feet (AF),and allowed water rights of 300 AF underSWRCB Water RightPermit No. 015913,and Lake Ada Rose has a storage capacity of 138 AFunderSWRCB Water RightPermit No. 014218, for a total available waterstoragesupplyfor the Districtof 389AF.(BTCSD:2018, 2019; LAFCo, 2010). | Good condition |  | C | 1. Compliance order for violation of section 116555 of CA Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 10/17/14
|  | BROOKWOOD MOBILE HOME PARK | 46037 | 1 |  |  | Other | Sonoma County | [28 empty] | Sonoma County |  | n
|  | BUCKTAIL MUTUAL WATER COMPANY | 30000 |  | 1 |  | Mutual | P.O. BOX 243 LEWISTON, CA 96052 | n | n |  | 32 | monthly/annual flate rate | Unfamiliar; disinterested | [21 empty] | Bucktail (a community within Lewiston), Trinity County. | Trinity | North Coast, Region 1 | n | 51 | GW | Wells (3) |  | 3 | Annual rate: $368/12 = $30.67 | $0 - $50
|  | BUD FINE MWC | 30000 |  | 1 |  | Mutual | [29 empty] | Trinity | North Coast, Region 1 | n
y | y | BURNT RANCH ESTATES Mutual Water Co. | 39167 | 1 |  |  | Mutual | PO Box 102 Burnt Ranch, CA 95527 | y | y | no | 35 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 1 | 3 | 3 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 3 |  | Burnt Ranch Estates, 35 households on Pony Express Way, Horseshoe Lane, and Stagecoach Road in Burnt Ranch | Trinity | North Coast, Region 1 | n | 115 | SW | IN - McDonald Creek - raw |  |  | 0-50 | $0 - $50 | [10 empty] | septic
y |  | BUTTE MOBILE HOME PARK | 26544 |  | 1 |  | other - mobile home park | 1010 BUTTE ST., CRESCENT CITY, CA 95531 | y | y | no | 23 | monthly/ annual flat rate | Unfamiliar; interested |  | 2 | 2 | 2 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 2 | 0 | 3 |  | Butte Mobile Home Park | Del Norte | North Coast, Region 1 | n | 67 | GW | Well (1) |  | 1 | 0-50 | $0 - $50
y |  | CAL ORE MOBILE ESTATES | 34000 |  | 1 |  | mobile home park | 1490 Kellogg Dr, Weed, CA 96094; and (2) Abrams Lake Mobile Estates, 2601 N Old Stage Rd, Mt Shasta, CA 96067 | y | n | y | 52 | monthly/ annual flat rate | Unfamiliar; disinterested |  | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 3 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 2 |  | Cal Ore Mobile Estates | Siskiyou | North Coast, Region 1 | n | 146 | GW | SP (1) | [8 empty] | A | 1. Violation of Total Coliform MCL | 1. 8/23/17
|  | California American GEYSERVILLE WATER WORKS (PUC) | 46250 | 1 |  |  |  | P.O. Box 65 GEYSERVILLE, CA 95441 |  |  |  | 308 | [24 empty] | Sonoma | North Coast, Region 1 | n | 875 | GW | Wells (3) |  | 3
| y | Green Diamond Resource Company - Korbel | 38816 | 1 |  |  | Other | Humboldt | n | y |  | 0 - 25 |  | Unfamiliar; interested | [14 empty] | 1 |  |  | 1 |  | 1 | 1 | Mill Site, Humboldt | Humboldt | North Coast, Region 1 | n | 0 - 25 |  |  |  |  | private system
|  | CALIFORNIA-AMERICAN WATER LARKFIELD (PUC) | 46037 | 1 |  |  | Public Utility | wikiup |  |  |  | 1803 | [24 empty] | Sonoma | North Coast, Region 1 | n | 5369 | GW | Water Purchases from SCWA; Wells ((5)
y | y | CALLAHAN WATER DISTRICT | 44242 | 1 |  |  | Water Dist | P.O. Box 1524/820 McKeen Rd. CALLAHAN, CA 96014 | y | y | no | 34 | monthly/ annual flat rate | Familiar; regular participant |  | 2 | 2 | 3 |  | 3 | 3 | 2 | 2 | n/a | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 2 | 1 | 3 |  | Callahan, CA | Siskiyou | North Coast, Region 1 | n | 70 | SW | Instream - West Boulder Creek - Raw |  |  | 0-50 | $0 - $50 |  |  |  |  | C | 1. Failure to monitor for coliform 2. Violation of section 116555 of the CA Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 4/12/13 2. 10/17/14 |  |  |  | septic
y |  | CALPELLA COUNTY WATER DISTRICT | 19356 |  | 1 |  | Water Dist | 151 Laws Avenue UKIAH, CA 95482 | no response | no | y | 176 | uniform rate schedule | Familiar; infrequent participation |  |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Calpella, CA | Mendocino | North Coast, Region 1 | n | 730 | Purchase | purchase treated water from Millview CWD and Redwood Valley CWD, also has a Well |  | 1 | 100-150 | $101 - $150 |  | The average normal year demand is 119 AF. The CCWD operates one well with a capacity of 40 AF and in order to meet demand must contract with RRFC for the remainder. Because of geographical constraints, the CCWD must contract with Millview County Water District for treatment and transport. Because of the uncertainty in water supply, the CCWD is under a new hookup moratorium. The Ukiah Valley Special Districts Municipal Service Review of 2013 recommended that Willow CWD, Calpella CWD, and Hopland PUD consider a formal consolidations through LAFCO. | Uncertain water supply | [7 empty] | sewer | [5 empty] | 1
|  | CANON MANOR WATER SYSTEM | 46037 | 1 |  |  | Other | [29 empty] | Sonoma |  | n
y |  | CASPAR SOUTH SERVICE COMPANY | 46037 | 1 |  |  | other | PO Box 744, Mendocino, CA 95460 | n | y | y | Water:42 connections Sewage: 32 connections to community septic system; 10 individual systems | Flat rate + variable usage charge | Familiar; not a participant | Unfunded | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | South Caspar, CA | Mendocino | North Coast, Region 1 | n | 188 | GW | Wells (8) |  | 8 | 100-150 | $101 - $150 |  | shallow wells | Uncertain water supply | [7 empty] | septic | Existing on-site community septic disposal system is inadequate; alternatives are being investigated using a Clean Water Program facilities planning grant The CSWD wastewater system was constructed in the early 1960’s as part of the subdivision’s initial development. The system consists of gravity fed connection laterals, collection tanks, screen separators, and a force main-fed leach field. District-owned treatment facilities were updated in 1982. These improvements consisted of a pumping station and installation of one large community leach field. At that time, the treatment plant located at the end of Otter Point Circle was de-commissioned, and subsequently served as a sewage collection tank. The District works to ensure the integrity of its system via testing and other measures including continual maintenance and monitoring, video camera inspection of lines, and locating and eliminating ‘wet areas’ where leaks are present . Through a series of ‘mini-projects’ (average cost of $15,000), the District is replacing worn-out lines. The most recent mini-project was replacing a 300-foot section of pipe in the southerly portion of the District. The District is also working to identify storm water intrusion sources. Through another series of small projects, the District has been working toward eliminating the intrusion problem. The District has also installed backflow prevention devices in each residential lateral, and has added two generators at each pump station in case of a power outage. Currently, the District is making system improvements including replacing aged pipes. CSWD has noted that its existing facilities are sufficiently sized to accommodate a total of 75 residential dwelling units. | Fair condition/ Upgrades planned/ identified |  | 1
|  | Caspar South Water District | 46037 | 1 |  |  | independent district | PO Box 744, Mendocino, CA 95460 | y |  |  | 66 |  | Familiar; not a participant | [21 empty] | Caspar, CA | Mendocino | North Coast, Region 1 | n | 185
y |  | CAZADERO WATER COMPANY, INC. | 49886 | 1 |  |  | Other | P.O. Box 423 6500 Cazadero Highway CAZADERO, CA 95421 | y | y | y | 157 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 0 | 0 | 2 | 1 | 2 | 2 | 2 | 0 | 0 | 1 | 0 | 2 |  | Cazadero, CA | Sonoma | North Coast, Region 1 | n | 250 | GU | 1 Spring, wells (4) |  | 4 | 0-50 | $0 - $50 |  | 1. As of October 2016, the Division hadn't received results for a routine bacteriological sample collected from the distribution system of the WC during August 2016. 2. System is in violation of permit by operating Buckeye and Hotel Wells year round; they are considered to be groundwater under the direct influence of surface water during rainy winter months and their use is restricted to between May 15 and September 15 in the system's water supply permit. Additionally, the system doesn't monitor raw water for bacteria monthly. 3. The Division hasn't received results for a routine bacteriological sample collected in 10/14. | Poor condition | Water board staff thinks the water is corrosive but that is questionable. | B | 1. Total coliform monitoring and reporting violation for August 2016 2. Compliance Order No. 02_18_17R_011 3. Total coliform monitoring and reporting violation for 10/14 | 1. 10/21/16 2. 7/7/17 3. 12/18/14 |  |  |  | septic
|  | Church Tree CSD | 26544 |  | 1 |  | CSD | 251 Church Tree Road, Crescent City, CA 95531 | n |  |  | 26 | Flat rate + variable usage charge | [22 empty] | east of Crescent City along Elk Valley Road and adjacent to the Jedidiah Smith Redwood State Park | Del Norte | North Coast, Region 1 | n | 40 | SW | purchases from City of Crescent City |  |  | 37.49 | $0 - $50 | Water from the Smith River is naturally filtered through the sand and gravel bed of the river and collected by intake lines 30 feet below the river. From there, water is pumped southward to the treatment facility off Kings Valley Road, where chlorine is added to meet State compliance standards. The City ceased adding fluoride on November 8, 2012 per ballot measure A | The Church Tree CSD receives water from the City of Crescent City. Crescent City obtains its water supply from the Smith River groundwater basin, which is located 8.5 miles north of the City. The basin produces approximately 2.9 million acre-feet of high quality water per year.Water is pumped out of the Smith River groundwater basin via a Ranney well, which has a capacity of 6,700 acre-feet per year. The District currently utilizes the following infrastructure: •One pump, •One 35,000 gallon water tank, •Approximately 10,00 lineal feet of water line, and •Two fire hydrants. The CTCSD’s water system is capable of serving 40 connections and is therefore operating at 65% of its total service capacity. The District water tank is currently not fenced and should be secured to comply with California code. The district should also plan on replacing the tank with hydrostatic pumps to maintain pressure and eliminate tank maintenance. (LAFCO 2018) | Fair condition/ Upgrades planned/ identified
y |  | CITY OF ARCATA | 28277 |  | 1 |  | City | City of Arcata 736 F Street ARCATA, CA 95521 | y | y | y | 6134 | Increasing block (graduated) rate schedule | Familiar; lack resources to participate | Funded | 0 |  | 2 |  | 3 | 2 | 0 | 0 | 0 | 2 | 0 |  | 1 | 2 |  | 1 |  | 2 | 3 |  | Arcata Bayside | Humboldt | North Coast, Region 1 | n | 19077 | GW | Purchases from HBMWD and Well (1) |  | 1 | 51-100 | $51 - $100 | All water introduced into the City's distribution system undergoes chlorination and fluoridation treatment. During the summer, this naturally filtered water is disinfected with chlorine. During the winter, it is further treated at a Turbidity Reduction Facility which reduces the occasional turbidity (cloudiness) in the source water. While turbidity itself is not a health concern, the State Water Resources Control Board (State Board) Division of Drinking Water (DDW) is concerned that at elevated levels, turbidity could potentially interfere with the disinfection process. | McKinleyville and the City of Arcata’s water supply are vulnerable to natural disaster, therefore, an emergency intertie was constructed to allow for the flow of water to occur between both systems if necessary. This line remains stagnant when not in use, therefore, a 5/8-inch bypass was installed which allows the water within the intertie to turnover and maintain its chlorine residual. All water that passes through the bypass is metered and currently enters into the City of Arcata’s water system from the McKinleyville system.” (McKinleyville CSD UWMP, 2015: P 13) | Adequate | Iron bacteria cause aesthetic water quality issues when our groundwater well is in operation. System performs frequent flushing to alleviate color & staining issues. |  |  |  | C | 1. NOV & transmittal of the 3/13 Compliance Evaluation Inspection Report. Deficiencies include: laboratory deficiencies; missing monitoring results, not recording effluent flow continuously, flow meters haven't been calibrated recently and calibration records couldn't be located. | 1.4/24/13 | sewer | The Glendale area receives wastewater service from the Fieldbrook-Glendale CSD. Glendale’s wastewater system is in very good condition overall and has approximately 166 connections. Flows currently range between 37,000 gpd during dry weather and 75,000 gpd during wet weather. The District has a contract to pump raw wastewater to the City of Arcata for treatment and disposal. The existing contract allows for up to 71,200 gpd average dry weather flow, indicating that the system has the capacity for approximately 80 to 100 more connections. Alternative solutions to treatment and disposal must be found to accommodate any development in excess of this. The City of Arcata has indicated it is not interested at this time in increasing the District’s contract amount and has recommended the District consider other alternatives. The District has approached the City of Blue Lake and will participate in other related studies to evaluate alternatives and costs for potential interconnection. | Good condition | The City of Arcata’s Best Management Practices for Stormwater Management considers runoff performance standards that result in site planning and design techniques to reduce storm flows, capture runoff water, and allow percolation or filtering before being discharged to channels, streams, or lakes. A significant portion of the manual information on Best Management Practices (BMPs) activities has been obtained from the California Stormwater Quality Task Force’s Best Management Practice Handbook and modified to suit the needs of the City of Arcata.
|  | CITY OF COTATI | 50667 | 1 |  |  | City | 201 West Sierra Avenue COTATI, CA 94931 |  |  |  | 2562 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Sonoma | North Coast, Region 1 | n | 7535 | GW | Purchased - SCWA - treated CC, wells (3) |  | 3 |  |  | The only required treatment is for bacterial and pathogen disinfection and pH adjustment. To accomplish this, the SCWA treats the water with chlorine for disinfection, and sodium hydroxide to adjust the pH before it is delivered to the various water dis-tricts and cities, including Cotati. | The City owns and operates a water supply and distribution system that supplies potable water to residences and businesses within the City limits. The City’s potable water supply comes primarily from water purchased from the Sonoma County Water Agency (SCWA) and water pumped from groundwater wells owned and operated by the City. The City’s main water supply is comprised of ground water from the Russian River permitted under a surface water diversion right for infiltration and groundwater from SCWA wells. In addition to the SCWA water supply, the City uses local groundwater supply from three municipal well sites located within city limits. Prior to 1992, the City used groundwater to supply more than half of its demands. More recently, the City’s water strategy has been to meet its demands by use of its SCWA water supply and to use its local groundwater supplies to supplement its needs during peak periods and during periods of drought. The City’s local groundwater supply is a key element of its drought contingency plan and is planned to remain as such throughout the 25-30 year planning horizon of the UWMP.4 The City actively seeks to balance the use of its SCWA water supplies and its local groundwater supplies in a way that ensures a sustainable yield of local groundwater. Additionally, as described in the UWMP, the City desires to implement a system that would allow for the delivery and use of recycled wastewater that is treated at the Santa Rosa Subregional System. There are currently three groundwater wells located within the City’s water distribution system. The City owns two water storage tanks. The West Sierra Avenue storage tank was constructed in 1997 and is a knuckle-roofed, welded steel storage tank with a total storage capacity of 1.0 million gallons. The facility is located west of Highway 101, just south of West Sierra Avenue, outside of the City limits. The tank has a base elevation over 249 feet and an overflow elevation of 274 feet. The high operating water surface elevation in the tank is 272 feet and the tank has a combined inlet/outlet pipe. The Cypress Avenue storage tank is a 100,000 gallon storage tank located at the end of Loma Linda Avenue. This storage tank is currently out of service; however the City plans to construct a new 400,000 gallon tank at this location in the future. | Fair condition/ Upgrades planned/ identified | [8 empty] | The City owns and operates a sanitary sewer collection system that provides sanitary sewer, or wastewater, service to approximately 1,200 acres in and around the City’s limits. The sanitary sewer system is comprised of four lift stations, approximately 140,300 lineal feet of collection piping ranging in size from six inches to 24 inches, approximately 484 manholes, approximately 150 cleanouts, and a 24-inch transfer interceptor which carries wastewater to the Santa Rosa Subregional Treatment Plant (also referred to as the Laguna Wastewater Treatment Plant) for treatment. The City’s Master Plan found that the current lift stations are capable of adequately conveying the existing and future (year 2035) design flow with the exception of the Quail Hollow Lift Station. However, the existing and future modeled capacity deficiency for this lift station was very minor. | Adequate
|  | CITY OF ETNA | 30089 |  | 1 |  | City | P.O. Box 460 ETNA, CA 96027 |  |  |  | 383 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 769 | SW | Instream
|  | City of Ferndale | 38750 | 1 |  |  | City | Ferndale, CA | y |  |  |  |  | Familiar; infrequent participation | Funded | [23 empty] | n | [18 empty] | Wastewater flows from the municipal collection system by gravity to the headworks. Within the headworks, a comminutor and bar screen provide primary treatment. Wastewater from the headworks of up to 0.95 MGD is then pumped to a selector tank flowing by gravity to one of two rectangular extended aeration basins for biological treatment. From the aeration basins, wastewater flows by gravity to the adjacent rectangular clarifiers. Return activated sludge (RAS) is injected into the selector tank and aeration basins as appropriate to achieve maximum nitrogen removal efficiencies. Aerobically digested sludge is then pumped to a belt press for dewatering. The dewatered sludge is transported to the Humboldt County solid waste transfer station for disposal to a landfill. Clarified wastewater undergoes disc filtration prior to ultraviolet disinfection. From October 1 through May 14, treated wastewater is discharged to Francis Creek at its confluence with the Salt River. From May 15 through September 30, treated wastewater for irrigation use is applied to neighboring agricultural land. Ferndale has been recycling its water since the new WWTF was completed in 2012. Facility improvement projects include: need for improved I&I, address issues with the equalizing storage pond, the UV disinfection system, and a composting facility. | Good condition | The City of Ferndale’s stormwater drainage system consists of a series of drainage inlets and underground pipes that eventually drain into the Salt River. Annual rainfall averages between40-60 inches. As mentioned previously, the hydraulic conditions of the Francis Creek / Salt River watershed have resulted in a higher sediment load and reduced flows that contribute to flooding during periods of peak stormwater runoff. This is further impacted by undersized drainage facilities and challenges re taining/detaining water onsite due to a high water table and relatively flat land. he city is currently in the early stages of updating its Drainage Master Plan to include watershed mapping, hydraulic modeling, and up-to -date stormwater infrastructure inventory to assess the current system condition and to identify drainage system improvements. This will incorporate watershed-wide restoration planning that is ongoing for Francis Creek and the Salt River.
|  | City of Fortuna WWTP | 49403 | 1 | [34 empty] | n | [15 empty] | Admin civil liability | 5.23.2018
y |  | CITY OF FORTUNA | 49403 | 1 |  |  | City | City of Fortuna P.O. Box 5 FORTUNA, CA 95540 | y | y | y | 4377 | Monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | 3 |  | Fortuna, CA | Humboldt | North Coast, Region 1 | n | 11649 | GW | Wells (5) |  | 5 | 100-150 | $101 - $150 | The City’s water supply comes entirely from five groundwater wells (four active and one emergency stand-by) located at the City’s corrosion control facility. The combined rated capacity of all wells is 4,000 gpm, or 5.76 MGD. Water is chlorinated in the wells as a precautionary measure due to the annular seals being less then 50 feet deep and then pumped from the wells into a 120,000 gallon wet well, containing three 100 horsepower booster pumps that pump water into the City’s distribution system. | The City’s water supply comes entirely from five groundwater wells (four active and one emergency stand-by). The well site includes disinfection and corrosion control facilities. It is believed that this water source is tied to the Eel River. The combined rated capacity of all wells is 4,000 gpm, or 5.76 MGD. Water is chlorinated in the wells as a precautionary measure due to the annular seals being less than 50 feet deep and then pumped from the wells into a 120,000 gallon wet well, containing three 100 horsepower booster pumps that pump water into the City’s distribution system. The distribution system is divided up into eight pressure zones and contains a series of pumps, water tanks, reservoirs, and hydropneumatic tanks. The combined storage capacity of the system is approximately 7.3 million gallons. Some pressure zones do not have adequate storage, but can be provided water through booster stations with portable generators on site. The city’s distribution system includes 37 miles of water piping. The system is composed of both new and old piping, with a mix of older asbestos-cement and cast-iron pipe, and newer polyvinyl chloride or PVC pipe. Water system infrastructure deficiencies have been addressed in the city’s five Year CIP. | Fair condition/ Upgrades planned/ identified |  |  |  |  | C | 1. NOV & transmittal of the 3/13 Compliance Evaluation Inspection Report. Deficiencies include: biosolids wasting rates insufficient to maintain system equilibrium; reporting erros including not reporting completed analyses and listing incorrect date for analyses. | 1. 4/24/13 | sewer | The City of Fortuna’s wastewater system is in good condition overall, and was expanded in 2006 to improve capacity and performance. The City’s wastewater facilities are permitted to treat up to 1.5 MGD mean daily dry weather flow averaged over a period of one calendar month. Existing dry weather flows are currently 0.95 MGD. Therefore, the treatment facility is operating at approximately 63% of its dry weather flow capacity. However, wet weather flows continue to pose a problem for the City. The most significant collection system issues relate to existing collection system pipingcapacities. The 12- and 15-inch sewer lines located between 9th and 12th Street, Loni Drive, and the area between I Street and L Street, respectively have flat grades and are subject to I/I. The old gravity lines located along Newburg Road are considered at capacity and not suitable for handling new or increased flows. There is also a lack of collection system piping in currently undeveloped areas. Wastewater system deficiencies are being addressed in the city’s Five-Year Capital Improvement Program. The 2007 – 2008 CIP lists eighteen wastewater projects to be completed over the next five years. | Fair condition/ Upgrades planned/ identified
y |  | CITY OF SANTA ROSA | 46037 | 1 |  |  | City | 69 STONY CIRCLE SANTA ROSA, CA 95401 | y | y | y | 52474 | Increasing block (graduated) rate schedule; For residential, there is a sewer base (amount of water in winter), Tier 2 is over and above that. For irrigation, Tier 1 is amount of water needed for landscape considering area and evapotranspiration, 125% of that rate is 2nd tier Flat rate for industry. Water and sewer combined, see above for how it's split, Colin can provide greater detail on all of this. Might be over $150, definitely not less than $100. Subsidized program for low - income residents using revenue from non-water sales and other income to reduce fixed rate charge and then do water efficiency work to reduce amount of water needed. | Familiar; regular participant | Funded | 0 | 1 | 2 | 0 | 2 | 2 | 1 | 0 | 0 | 1 | n/a | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | Santa Rosa, CA | Sonoma | North Coast, Region 1 | n | 178488 | GW | purchase treated from Wohler Cassion, spring (1), wells (4) |  | 4 | 100-150 | $101 - $150 | Water collected from the Russian River through deep collector wells requires no additional treatment with the exception of chlorine which is added for disinfection, and sodium hydroxide which is added to adjust the pH of the water to reduce corrosion of lead and copper plumbing fixtures. |  |  | With water supply wells, there is a taste and odor issue with sulfur and manganese - about 5 - 10% of water use - during April -October when there's high demand. Water from SCWA - no issues primary or secondary. well issues only secondary. | [6 empty] | sewer
|  | COPCO LAKE MWC | 40938 | 1 |  |  | Mutual | 16238 VALERIE RD. MONTAGUE, CA 96064 |  |  |  | 65 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 181 | GW | SP - spring, raw, and well
|  | COVE MOBILE VILLA | 25493 |  | 1 |  |  | 6431 Old Hwy 99 S, Yreka, CA 96097 |  |  |  | 70 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 128 | GW | Well |  | 1
y | y | COVELO C.S.D. | 29167 |  | 1 |  | CSD | 76270 Grange Street (P.O. Box 65) COVELO, CA 95428 | y | y | y | 265 | Monthly/ annual flat rate | Familiar; infrequent participation | Funded | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Covelo, CA | Mendocino | North Coast, Region 1 | n | 1255 |  |  | ~ 481 (# of households) |  | 51-100 | $51 - $100 | [10 empty] | sewer | The CCSD sewer system consistsof four major collection basins; threeof them north of Town Creek, and the other south of the creek. The smallest of the three northern basins lies along East lane within the northeast corner of the CCSD. Wastewater in this basin flows by gravity to a lift station near the northern limit of the Commercial Street sewer main. The lift station pump ... lifts collected wastewater to the terminal manhole on the Commercial Street main where it joins wastewater generated in the largest northern collection basin situated within and west of Commercial Street.The largest collection basin located north of Town Creek and primarily west of Commercial Street includes contributors from parcels near the intersection of Howard Street and Crawford Road at the extreme northwest side, and from the contributors within the more urban area bounded by Howard Street on the north and Commercial Street on the east. All wastewater from these two northern collection basins flows by gravity toward Town Creek, and passes under the creek through an inverted siphon. A main interceptor sewer line located just south of Town Creek conveys collected wastewater east to the wastewater treatment plant. The overall collection system serves a geographic area of about 185 acres, including approximately 35 acres that lie outside of the existing district boundary. The collection system service area contains approximately 200 residential users, 51 commercial users, 9 institutional users, 2 public uses, and 2 other uses that do not fit a standard user category. The sewer main piping comprising the collection system in the largest of the three northern basins includes approximately 3,900 linear feet of 8-inch diameter and 14,575 linear feet of 6-inch diameter asbestos-cement pipe (transite pipe). There are approximately 45 manholes and 10 mainline cleanouts in this portion of the overall system. Originally, the collection system flowed towards Commercial Street, and flowed south to a point 1500 feet south of Elberle Street where it turned eastcrossing under Town Creek a second time to the treatment plant. In 2007, the Town Creek Bridge was bypassed with 654 feet of twelve inch line that directs sewage from north of Town Creek straight to the plant. The old line passing under the bridge was plugged.From the new manhole just north of the bridge to the manhole at Commercial and Howard Streets, 2,064 feet of sewer line were replaced with 10 inch SDR-26 PVC pipe. All 2,657 feet of sewer line on Howard Street was replaced with 8 inch SDR-26 PVC. Sewer line replacement included new manholes. In its 2006 report, SHN Engineers listed a number of plant deficiencies:Grit, rocks, rags and other damaging materials were not effectively removed from the effluent flow. Equipment is damaged and ponds fill up with these materials requiring significant dredging.Headworks and pretreatment processes were significantly problematic. The headworks structure was much too small to allow proper maintenance of equipment. The comminutor was outdated, doesn’t work, and needed replacement. New equipment to remove more of the damaging materials entering the system was needed.The septage receiving system at that time relied on self-monitoring of septage haulers regarding quantity, pH, etc. SHN recommended an automated septage receiving system be installed.The two oxidation ponds suffer from varying degrees of seepage through their walls caused by rodents, roots, etc. At the time of the report groundwater tests were still being conducted to determine if the seepage through the pond bottoms was significantly affecting groundwater quality.Both holding ponds typically dry out during hot summer months, when practically all the treated effluent is evaporated from the oxidation ponds. This has caused the bentonite linings to crack and leak. When the ponds receive treated effluent it leaks uncontrollably into the groundwater. Attempts to keep the bottoms of the ponds moist during the hot months have not been effective because of an inadequate supply of well water and the inability to apply the water evenly across the surface.In recent years evaporation and seepage from the oxidation and holding ponds has all but eliminated the need to discharge treated effluent into Grist Creek. As a result the final filtering and disinfection systems have not been used in many years. This has led to significant problems with the pumping,filtering and disinfection systems. A number of significant public health threats are caused by the District’s sewer system. Elementary School -raw sewage has overflowed out of the system in front of the school for 30 years.Overflow in Other Locations -At least two other locations had occasional overflows out of the system into streets.Back up into Homes -homes in two areas of the District occasionally had sewage backing up flowing into their yards.These problems mostly happen during storms.SHN states that both capital improvements to the system and upgraded maintenance practices are needed to correct these problem. The majority of effluent disposal occurs through percolation into the groundwater beneath the holding ponds, which is in violation of the District’s existing NPDES permit5.The uncontrolled percolation that is occurring at present does not adequately protect the quality of groundwater underlying the plant area. CSD has been busy in recent years correcting numerous problems with their collection system. The remaining system problems noted above create significant constraints on the ability of staff to properly maintain the system. The “solutions” to the indicated problems are mostly investment in upgraded facilities; the difficulty is in obtaining sufficient funds for the “solutions”. | Poor condition
|  | COVELO MOBILE HOME PARK | 29167 |  | 1 |  | other |  |  |  |  | 19 | [24 empty] | Mendocino | North Coast, Region 1 | n | 30 | GW | Wells (2) |  | 2
y |  | COVINGTON MILL MWC-DIVISION B | 32321 |  | 1 |  | Mutual | P.O. BOX 144 TRINITY CENTER, CA 96091 | n | y | dk | 99 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 0 | 1 | 1 | 0 | n/a | n/a | 0 | 0 | 0 | 1 | 0 | 0 |  | 1 | 0 | 0 | 1 | 3 | 2 | 1 | CMMWC, B. Hwy and Lake Forest Drive | Trinity | North Coast, Region 1 | n | 99 | GW | Wells (7) |  | 7 | 0-50 | $0 - $50
|  | Creekside Cabins & RV Resort | 45299 | 1 |  |  |  | PO Box 279, Lakeport, CA 95453 |  |  |  | 55 | [24 empty] | Mendocino | North Coast, Region 1 | n | 124 | GW | Well |  | 1 | [6 empty] | 0 | 1. Bacteriological monitoring violation | 2015-12-15
y | y | CRESCENT CITY, CITY OF | 26544 |  | 1 |  | City | 377 J STREET CRESCENT CITY, CA 95531 | y | y | y | 3416 | uniform rate schedule | Familiar; regular participant | Funded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 |  | Crescent City, CA | Del Norte | North Coast, Region 1 | n | 15600 | GW | Well |  | 1 | 51-100 | $51 - $100 | Using natural filtration through the sand and gravel bed 30 feet below the river, water is collected from intake lines (or fingers) driven into the gravel bed. Water is pumped southward to the treatment facility off Kings Valley Road, where chlorine is added to meet State standards. This is the extent of treatment. The City of Crescent City ceased adding fluoride to its water supply on November 8, 2012 per ballot Measure A. Water from the Smith River is naturally filtered through the sand and gravel bed of the river and collected by intake lines 30 feet below the river. From there, water is pumped southward to the treatment facility off Kings Valley Road, where chlorine is added to meet State compliance standards. The City ceased adding fluoride to its water supply on November 8, 2012 per ballot measure A. Under Water Resources Control Board water rights permits, the appropriation from the Smith River (underflow) is specified as an average of 12.8 cubic feet per second (cfs) (8.3 million gallons per day) with a maximum annual diversion of 3,666 AFY (1,194 million gallons per year) (Freshwater Environmental Services, 2014. | Crescent City Adopted MSR/SOI 10 2019 The CCHA is developing an affordable housing project with Project Based Vouchers (PBVs) as a partial funding source. They have secured property, committed vouchers and selected a contractor, Danco Communities, and entered into a deferred development agreement to build the “Harbor Point Apartments” an affordable housing project with subsidized units. Water Services. The Crescent City water system provides water collection, treatment and distribution to the incorporated city of Crescent City, certain unincorporated areas near the city, and the Pelican Bay State Prison through a system comprised of one well in the Smith River, and 60 miles of water mains. Under contractual agreements, the City also delivers water within the Bertsch-Oceanview Community Services District (BOV CSD), the Church Tree Community Services District (CT CSD), Crescent Fire Protection District W-1 (FDW1) and the Meadow Brook (MB) area of the Del Norte Flood Control District. The Smith River provides an abundant supply of high quality fresh water. | Adequate |  |  |  |  | C | 1. Administrative Civil Liability Complaint: Discharger's self-monitoring reports for the complaint period document seven violations of effluent limitations. All seven violations are subject to MMPs. 2. Order No. R1-2017-0002, Waste Discharge Requirements and Water Recycling Requirements for the City of Crescent City Wasteater Treatment Facility, Del Norte County | 1. 7/22/2016 | sewer | Major renovations and upgrades to the Crescent City wastewater treatment facility were completed in 2010. The Wastewater Treatment Facility (WWTF) consists of new influent pumping equipment and controls, new grit removal system, primary clarifier modifications, upsized and upgraded site piping, removal of underground storage tank and contaminated soil, and addition of membrane bioreactors, ultraviolet disinfection and effluent pumping for the production water that comports with the California Code of Regulations Title 22 (Title 22)requirements.The City's WWTF is capable of producing, tertiary-treated recycled water meeting Title 22 Water Recycling Criteria and the City looks for recycled water use opportunities. The reclamation system capacity is 0.6 mgd; however, the membrane bioreactor can treat up to 1.6 mgd. Effluent that is not recycled is discharged to the Pacific Ocean. The 24- inch diameter ductile iron pipe outfall discharges into a rocky slot in the surf zone adjacent to Battery Point Lighthouse and has an effluent conveyance capacity up to 13 mgd (UWMP). | Good condition
| y | DEL NORTE COUNTY COMMUNITY SERVICE AREA | 26544 |  | 1 |  | County Dist | 981 H STREET, SUITE 101, CRESCENT CITY, CA 95531 | y | y |  | 2000 | monthly/ annual flat rate | Familiar; regular participant | Funded | [5 empty] | 1 | [10 empty] | 1 |  |  |  | Unincorporated areas of Del Norte County. | Del Norte |  | n | 6000 |  |  |  |  | $6.50/ month | $0 - $50
|  | DELORES LANE WATER SYSTEM | 46037 | 1 |  |  | other | 1746 Olivet Road SANTA ROSA, CA 95401 |  |  |  | 17 | [24 empty] | Sonoma | North Coast, Region 1 | n | 50 | GW | Wells (2) |  | 2
|  | Dolphin Isle Marina | 31027 |  | 1 |  |  | 32399 Basin St. FORT BRAGG,CA 95437 |  |  |  | 85 | [24 empty] | Mendocino | North Coast, Region 1 | n | 560 | GW | Well |  | 1
y | y | DORRIS, CITY OF | 31923 |  | 1 |  | City | P. O. BOX 768 (307 S. Main Street) DORRIS, CA 96023 | y | y | y | 481 | monthly/ annual flat rate | Familiar; lack resources to participate | Unfunded | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | N/A | 3 | 2 | 2 | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 2 | Dorris, CA | Siskiyou | North Coast, Region 1 | n | 887 | GW | Wells (2) |  | 2 | Majority of services Resid water-41.75 month/Resid sewer-18.25 Comm1 water-29.04 Sewer 11.62. We have a few like school, clinic and mill that are a higher rate 51-100 | $51 - $100 |  |  |  | City has to treat for smell problem; Strong sulfur odor |  | 1. Citation for violation of the coliform MCL January 2013 | 1. 3/29/2013 |  |  |  | sewer
|  | Dos Rios Mutual Water Company | 23315 |  | 1 |  | Mutual | 11801 Dos Rios Road, Dos Rios, CA 95429 | n |  |  | 24 | [23 empty] | Dos Rios, CA | Mendocino | North Coast, Region 1 | n | 21 | GW | Well (1) Inactive |  | 0 | $41 - $80 per month | $51 - $100 |  | The Company owns and maintains one well and approximately four to five miles of pipeline. | Adequate
|  | EAST AUSTIN CREEK MUTUAL WATER COMPANY | 49886 | 1 |  |  | Mutual | [29 empty] | Sonoma |  | n |  | GW | Well (1) |  | 1
|  | EL CRYSTAL MOBILE HOME PARK | 46037 | 1 |  |  | Other | 3280 Santa Rosa Ave, Santa Rosa, CA 95407 |  |  |  | 58 | [24 empty] | Sonoma | North Coast, Region 1 | n | 130 | GW | Wells (2) |  | 2 | [6 empty] | A | 1. Compliance Order 02_18_17R_009 | 1. 6/23/17
|  | EL PORTAL MOBILE ESTATES | 29250 |  | 1 |  | Other | 871 38TH AVENUE SANTA CRUZ, CA 95062 |  |  |  | 122 | [24 empty] | Sonoma | North Coast, Region 1 | n | 200 | GW | Wells (2) |  | 2 | [6 empty] | C | 1. TCE MCL Violation for third and fourth quarter 2014 | 1. 2/19/17
|  | ELK COUNTY WATER DISTRICT | 39667 | 1 |  |  | Water Dist | PO Box 195, Elk, CA 95432 Alternative Address: 6129 S Highway 1 Elk, CA 95432 | y |  |  | 101 | increasing block | [22 empty] | Elk, CA | Mendocino | North Coast, Region 1 | n | 380 | GU | Wells (2) |  | 2 |  |  |  | ECWD’s water system is classified as a ‘community water system’ and includes a water treatment plant (WTP), one well, and several miles of pipeline. The District does not own any major equipment. The District owns the following infrastructure:  water treatment plant;  two water storage facilities – 30,000 and 84,000 gallons  pipes;  One new supply well;  parcel of land where the well is located (one parcel is owned and ECWD has an easement over the second parcel); and  parcel of land that houses a storage shed, community center, and volunteer fire station. Projects or impacts to Greenwood Creek have the potential to negatively affect the District’s water supply. For example, a project to replace the Greenwood Creek Bridge resulted in temporary impacts to the District. | Adequate | [8 empty] | The WTP uses direct filtration to remove 99 percent of Giardia lamblia cysts and 90 percent of viruses. | Adequate
| y | END-O-VALLEY MUTUAL WATER COMPANY | 46037 | 1 |  |  | Mutual |  | n | n |  | 25-50 | monthly/ annual flat rate | Unfamiliar; disinterested | [14 empty] | 1 |  |  | 1 |  |  | 1 |  | Sonoma | North Coast, Region 1 | n | 100-250 |  |  |  |  | $50-100 | $51 - $100
|  | EUREKA, CITY OF, ELK RIVER WWTP | 20346 |  | 1 | [33 empty] | n | [15 empty] | Admin Civil Liability | 2018-06-07
y | y | EUREKA, CITY OF | 20346 |  | 1 |  | City | 3575 W Street, EUREKA, CA 95501 | y | y | y | 9944 | Uniform rate schedule with volume charges | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 0 | 0 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 2 |  | Eureka, CA | Humboldt | North Coast, Region 1 | n | 32815 | GWP | purchase treated from HBMWD |  |  |  |  | The City’s water treatment plant provides chlorination and fluoridation treatment. | The City of Eureka purchases water from a wholesaler, Humboldt Bay Municipal Water District. Under the agreement between the District and The City of Eureka, the deliveries from the District to the City are considered to be deliveries of the City's water, emanating from its own water rights not those of the District. Deliveries to the City in excess of the City's water rights are considered deliveries of the District's water. Water is supplied to two primary pressure zones: the Low Zone and the High Zone. A 24-inch steel main supplies the low zone by gravity, and a 16-inch steel force main supplies the high zone with pumping. The high zone pumping capacity is 2,400 gallons per minute (GPM). The low zone is fed by gravity from the 20-MG reservoir, with an increased capacity flow of up to 6,000 GPM when using two 50-HP vertical turbine pumps and one backup 100-HP pump. The system’s total storage capacity is 22.3 MG, comprised of a 20-MG raw water storage reservoir, a 1-MG ground-level steel tank, a 500,000-gallon ground-level steel tank, a 500,000-gallon elevated steel tank, and a 300,000-gallon clear well. The City’s distribution system has normal deficiencies for a system of its age, which includes an aging piping system and low-pressure and fire-flow issues. Planned water distribution system improvements within the City include the following: Repairs and replacement of deteriorated, undersized, and aged mains, valves, and services in accordance with the Water Distribution System Annual Replacement and Maintenance Program Planned water treatment system improvements Corrosion control and upkeep of water storage tanks A new pump station at the Harris and K Streets tank farm Replacement of fire hydrants that do not meet the City’s current standards for fire flow capacity Installation of water meters at all City facilities | Fair condition/ Upgrades planned/ identified | [7 empty] | sewer | The City’s wastewater collection system contains approximately 125 miles of sewer main, 9,500 service laterals, 18 lift stations, 4 major pump stations, and associated force mains. The system collects and conveys between 1.6 and 1.8 billion gallons of wastewater per year. The City also collects wastewater from HCSD, which serves the unincorporated areas east and southeast of the city limits. The City operates the Elk River Wastewater Treatment Plant (WWTP) located in the southwest portion of the City near the mouth of the Elk River; the WWTP was designed in 1981 for the purpose of treating, storing, and disposing of wastewater. The WWTP serves customers within the City of Eureka and also treats wastewater from the surrounding unincorporated areas served by HCSD. The total City, County, and HCSD population served by the WWTP is approximately 45,000. The City’s wastewater collection system is experiencing deficiencies that are typical of a collection system of its age, including Inflow and Infiltration (I/I), pipe condition deterioration (with a majority being clay pipe), aging pumping systems, and some capacity limitations. Capacity concerns occur at a few locations in the collection system during significant rain events. The City has planned the following WWTP and collection system upgrades: Wastewater Collection System Replacement and Maintenance Program Implementation Wastewater Inflow and Infiltration Reduction Program - A multi-phased, multi-year program for reducing I/I into the wastewater system by implementing capital improvement projects in accordance with program recommendations based on field tests. Sewer Lift Station and Pump Station Upgrades including a change to VFD pump control Extended Fuel Storage Facility Cross-town Interceptor Maintenance Installation, Replacement, Repair, or Relocation of Storm Drainage Facilities City-wide. | Fair condition/ Upgrades planned/ identified | Much of the City’s existing storm drainage network is old and undersized, depending upon inadequate gutter flow and undersized pipes and drop inletsxvii. There is street flooding during the rainy season. Some of the City’s sloughs and gulches, serving as natural drainage networks, have been filled, restricted, and/or altered. Most of the natural networks are unimproved, relatively deep, and have adequate capacity for a 100-year storm event. However, due to erosion and siltation, resulting in reduced capacity at some storm drain inlets and outlets, a few of the gulches experience flooding. No actual drainage easements exist for many of the City’s natural drainage networks; due to lack of access, maintenance and replacement within these gulches can be difficult. (LAFCO) The City of Eureka’s Storm Water Quality Management and Discharge Control Ordinance, contains detailed BMP requirements that are comprehensive, are consistent with the Federal Clean Water Act and the Porter-Cologne Water Quality Control Act , and are a very effective means of reducing stormwater pollution that are a result of development activities.
|  | FERNDALE - DEL ORO WATER CO. | 38750 | 1 |  |  | Public Utility | DRAWER 5172 CHICO, CA 95927 | y |  |  | 759 | increasing block | [23 empty] | Humboldt | North Coast, Region 1 | n | 1998 | GW | Springs - raw (2), well |  | 1 | wastewater = 66.02/month | $51 - $100 |  | Ferndale water sources originate from groundwater and are known as the High Line Springs, Low Line Springs, and Van Ness Well. These sources have a combined maximum production capacity of approximately 518,000 gallons per day. As of 2012, existing maximum daily demands are estimated at 208,000 gallons per day, which is approximately 40% of source capacity. Approximately 70% of the water is pulled from the springs, with back up production from the Van Ness Well. | Adequate | [12 empty] | 1
y | y | FIELDBROOK GLENDALE C.S.D. | 20346 |  | 1 |  | CSD | PO Box 2715, McKinleyville, CA 95519 P.O. BOX 95 EUREKA, CA 95502 | y | y | y | 584 | Monthly/ annual flat rate; Increasing block (graduated) rate schedule | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  | Fieldbrook & Glendale | Humboldt | North Coast, Region 1 | n | 1927 | GWP | CC Humboldt Bay MWD purchased |  |  | Water $45 Wastewater $76 | $101 - $150 | purchases treated water from HBMWD | The Fieldbrook-Glendale CSD’s receives treated water through the HBMWD and is not limited by either source or treatment capacity with respect to its ability to serve new connections. The only major deficiency associated with the existing system and the existing development they serve is lower than desirable water pressure within some localized areas. In addition, a stand by generator is needed at the main (Lyman Rd) booster pump station and a new roof is needed on the redwood tank. The Fieldbrook-Glendale CSD may need to expand its water distribution system at some point to serve this additional growth. The Fieldbrook-Glendale CSD purchases treated water from Humboldt Bay Municipal Water District (HBMWD) for delivery to its customers. The FGCSD system begins at a water meter just north of the intersection of Fieldbrook Road and includes over 10 miles of water mains, one booster pump station, and one 400,000 gallon water tank. Water quality is excellent and meets or exceeds State standards. Some localized pressure problems are experienced by some residences and this problem needs to be addressed before any additional growth is to occur. Other water system improvements anticipated to be needed include the installation of a standby (emergency) generator at the booster pump station and the construction of an additional reservoir. In the Glendale area, low water pressure is among the primary concerns voiced by local residents. Water service within the Glendale area is generally very good, with the exception of some low pressure areas. The only major deficiency associated with the existing system and the existing development they serve is lower system pressure within some localized areas. The Glendale area does not have any storage in its service area and normally relies on the HBMWD water reservoirs, although the Fieldbrook reservoir can be used to back feed to this area in an emergency. The Blue Lake FPD Fire Chief, who has fire protection responsibility for most of Glendale, states that additional water storage is required within Glendale for fire suppression as well as domestic water needs (Personal Communication, January, 2017). Glendale will need to expand its water system infrastructure to serve additional growth. The Fieldbrook-Glendale CSD receives treated water through the HBMWD and is not limited by either source or treatment capacity with respect to its ability to serve new connections. | Good condition | [7 empty] | sewer | The Glendale area receives wastewater service from the Fieldbrook-Glendale CSD. Glendale’s wastewater system is in very good condition overall and has approximately 166 connections. Flows currently range between 37,000 gpd during dry weather and 75,000 gpd during wet weather. The District has a contract to pump raw wastewater to the City of Arcata for treatment and disposal. The existing contract allows for up to 71,200 gpd average dry weather flow, indicating that the system has the capacity for approximately 80 to 100 more connections. Alternative solutions to treatment and disposal must be found to accommodate any development in excess of this. The City of Arcata has indicated it is not interested at this time in increasing the District’s contract amount and has recommended the District consider other alternatives. The District has approached the City of Blue Lake and will participate in other related studies to evaluate alternatives and costs for potential interconnection. | Good condition |  | 1 | 1
|  | Forestville Water District | 38792 | 1 |  |  | Water Dist | [29 empty] | Sonoma | North Coast, Region 1 | n | [12 empty] | Category 1 Pollutant (Effluenct Violation for Group 1 Pollutant) | 1/31/2019, 1/22/2019; 2/14/2019; 2/28/2019; 3/12/2019
| y | FORT BRAGG MUNICIPAL IMP DISTRCT | 31027 |  | 1 |  | Municipal Imp Dist | 416 N. FRANKLIN ST., FORT BRAGG, CA 95437 | y | y |  | 2800 | Monthly/ Annual Flat Rate: Monthly flat rate that increases by unit. | Unfamiliar; interested | [6 empty] | 1 | [10 empty] | 1 |  |  | 1 | Fort Bragg, Mendocino County. | Mendocino | North Coast, Region 1 | n | 7000 | [17 empty] | The public wastewatertreatment system includes collection, treatment, and discharge facilities. The wastewater system serving the City of Fort Bragg is owned by the Fort Bragg Municipal Improvement District (MID/District)No. 1 and isoperated and maintained by the Cityat the expense of the District. The District boundary is larger than the City boundary. The Fort Bragg MID No. 1(District)was formed to acquire and construct wastewater system improvements including a wastewater treatment plant and to provide for the incurring of indebtedness for the costs and expansion of such improvements. Any territory annexed to the MID is subject to all the liabilities, including previously authorized taxes, benefit assessments, fees or charges for services, and is entitled to all benefits of the District. (LAFCo, 2008)The Wastewater Treatment Plant (WWTP) is located at 101 West Cypress Street in Fort Bragg. The WWTP operates under Waste Discharge Requirements pursuant to Order No. R1‐2015‐0024, NPDES No. CA0023078, and WDID No. 1B84083OMENissued by the North Coast Regional Water Quality Control Board on June 4, 2009 (Fort Bragg, March 2017). The MID serves approximately 2,450 residentialwastewaterconnections,350commercial dischargers,and one industrial customerwithin the District,and serves MacKerricher State Park located outside the District(Fort Bragg, July 2017). The MID wastewater system is comprised of over 25 miles of gravity-fed pipelinesand pressure force mains, six sewage lift stations,theWWTP,and an ocean outfall pipeline that extends690 feet into the Pacific Ocean. Over the past five years, the North Coast Regional Water Quality Control Boardh as issued two settlement agreements for Administrative Civil Liability (ACL)to the District, both were satisfactorily addressed. The most recent ACL (R1-2016-0049) consists of two compliance projects to satisfy the minimum mandatory penalties. These exceedances include biochemical oxygen demand (BOD), total suspended solids (TSS), Total Coliform and Total Chlorine Residual. The compliance projects involve installation of an influent flow meter and installationofsodium hypochlorite and sodium bisulfite analyzers. The previous ACL (R1-2014-0035) included a compliance project to complete the designphaseof the WWTPUpgrade Projectin order to improve BOD and TSS effluent discharge. These compliance projects have been completed, with the exception of the influent flow meter which is scheduled for installation in September, and satisfactorily addressed the RWQCB concerns.(Fort Bragg, March 2017; Fort Bragg, July 2017) Currently, the WWTP wet weather treatment capacity is exceeded several times a year due to very high flows of stormwater and groundwater into the wastewater collection system caused by infiltration and inflow (I/I) and cross-connection between storm drains and sewer lines. I/I is problematic for multiple reasons but especially because of the potential for sanitary sewer overflows (SSOs) and penalties for exceeding effluent limitations when the WWTP cannot operate as designed. The aging infrastructureof the wastewater system and the peak flow volume during wet weather events are the primar yfactors influencing the District’s ability to provide wastewater services to customers. | Storage capacity insufficient
|  | Fort Bragg City WWTP | 31027 |  | 1 | [33 empty] | n | [15 empty] | Expited Payment Letter | 6.16.17
y | y | FORT BRAGG, CITY OF | 31027 |  | 1 |  | City | 416 N. FRANKLIN STREET FORT BRAGG, CA 95437 | y | y | y | 2822 | Seasonal rate schedule | Familiar; infrequent participation | Unfunded | 0 | 2 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 2 |  | Fort Bragg, CA | Mendocino | North Coast, Region 1 | n | 7250 | SW | IN - Newman Gulch Intake, Noyo River Pump Station, Simpson Creek Intake |  |  | 100-150 | $101 - $150 |  | The City’s water system is comprised of three surface water sourcesincluding the new Summers Lane Reservoir constructed in 2015; threeraw water transmission mains; two raw water storage ponds located at the WTP; the WTP that was originally constructed in the 1950’s and upgraded in the 1980’sand has a capacity of2.2 million gallons per day (MGD); two 1.5 million gallon (MG) steel storage tanks and one 300,000 gallon storage tank; over 30 miles of distribution lines that deliver water throughout Fort Bragg; and one booster pump station for the East Fort Bragg pressure zone (LAFCo,2008). Additionally the City has funding for and will add an additional1.5 million gallon finished water storage tank in Fiscal Year 2017-18. (LAFCo,2008; Fort Bragg, July 2017) The City’s water supply system draws raw water primarily from the Noyo River with the limitation that pumping does not exceed 3.0 cubic feet per second (cfs).The Noyo River direct diversion flows by gravity into a 5,000 gallon wet well and is then pumped via pipeline to the WTP from a pump station on the river bank.The Newman Reservoir is an on-stream reservoir located on a 54-acre parcel owned by the City of Fort Bragg and impounds water from the Newman Gulch. The Summers Lane Reservoir is a new reservoir with a capacity of 45 acre-feet (AF) located on this same property. The Summers LaneReservoir is an off-stream storage facility that holds water from Waterfall Gulch .Approximately 20% of the City’s water supply during the summer months is drawn from the Newman and Summers Lane Reservoirs and approximately 25% throughout the year is from the Waterfall Gulch diversion, all of which are gravity fed through a single ten-inch pipeline to the raw water storage ponds at the WTP. (LAFCo,2008; Fort Bragg, July 2017). The aging infrastructure of the water system and the reliability of the water collection conduits are the primary factors influencing the City’s ability to provide water services to customers. | Fair condition/ Upgrades planned/ identified | [5 empty] | Fort Bragg City WWTP; Expedited Payment Letter | 2017-06-16 | sewer | The City public water system includes raw water collection,treatment, and distribution facilities,which are owned and operated by the City. The Water Treatment Plant(WTP)is located at 31301 Cedar Street in Fort Bragg. | Adequate | The priority storm drain improvements in the 2004 Storm Drainage Master Plan have been implemented. Much of the area north of Pudding Creekand south of the Noyo River generally do not have improved drainage systems in place. Drainage in these areas is generally throughnatural channelsor site installed drainage pipes.Chapter 12.14, 17.60 and 18.60 of the City's Municipal Code require the City to reviewand conditionnew development to ensure that adequate on-site and off-site drainage is included in the development.New development is required to paya drainage impact fee and therebyfund improvements necessary to ensure adequate capacity within the storm drain system. (Fort Bragg, 2012c; Fort Bragg, July 2017) |  |  | 1
| y | FORT JONES, TOWN OF | 45365 | 1 |  |  | City | P.O. BOX 40, FORT JONES, CA 96032 | n | y |  | 366 | monthly/ annual flate rate | Familiar; not a participant | [5 empty] | 1 | [7 empty] | 1 |  |  |  | 1 |  | 1 |  | Town of Fort Jones | Siskiyou | North Coast, Region 1 | n | 675 | GW | Wells (3) |  | 3 | 35 min./water 15 sewer | $51 - $100
| y | GARBERVILLE SANITARY DISTRICT | 36371 |  | 1 |  | Sanitary Dist | P.O. BOX 211 GARBERVILLE, CA 95542 | y | y |  | 442 |  | Familiar; infrequent participation | Unfunded |  |  |  |  | 1 | 1 | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  | Garberville , Humboldt | Humboldt | North Coast, Region 1 | n | 1500 | SW | Instream - Eel River, Well |  | 1 | residential water - 66.89 residential wastewater - 47.70 Water- Variable Base and Variable Usage base rate is by meter size and usage rate is by amount used. Wastewater - fixed base and variable usage. residential usage based on the months of Jan-Mar. Commercial base rate based on 90% of last years usage and usage rate based on 90% of last months usage for each strength. | $101 - $150 | The water treatment facility produces water that meets or exceeds the State regulations for drinking water. The turbidity and residual free chlorine levels comply with the maximum allowable levels, treatment occurs in highly efficient chlorine contact chamber. | Presently, the District maintains and operates a water system and a sewer system. The water system was recently purchased from private owners and consists of two water sources, a treatment plant, four water tanks, three booster stations, approximately 380 active service connections, and a waterline distribution network. One of the water sources is surface water from the South Fork of the Eel River and one is a shallow well in downtown Garberville. The surface water source is regulated by the California Surface Water Treatment Regulations. The existing system has adequate production, treatment, and storage capacities for the average daily demand. The maximum daily demand is 370,830 gpd based upon the maximum month of July 1999. The total storage capacity for the system is approximately 300,000 gallons. This is not sufficient to meet the maximum daily demand or to provide any fire protection services during the maximum daily demand. The existing system provides adequate water pressure throughout the District. Reports of inadequate flow for fire suppression purposes have been received for Maple Street. This is likely due to insufficient line sizes. The system in general has very few fire hydrants, and many of those installed are wharf hydrants that will not provide sufficient flow for fire suppression. The fire department reported that there are only a few hydrants that are approved for use during a structure fire, and most are located on Redwood Drive. The Eel River Infiltration Gallery is the main water source and it is a surface water source. It was originally installed in 1940. The infiltration gallery has one 6-inch 320-gpm 50-HP submersible pump that was installed in February 1999. The pump operates against an approximate 380 feet differential elevation head. The pump discharges to the water treatment plant adjacent to the 200,000-gallon storage tank. The pressure filter in the water treatment plant has a limited capacity of 250 gpm. The existing treatment plant filtration cell does not have sufficient capacity to allow processing of the maximum daily demand. The treatment plant produced a total of 80 million gallons of water in 1999. The majority of the water mains in downtown Garberville were installed prior to 1940. Some of the lines are lead joint, some are copper, and most are either iron or asbestos cement. Only the line in Redwood Drive is 8 inch. Most of the downtown mains are 4-inch lines. The water mains in the Wallen and Johnson Subdivision were installed in 1978 and are mostly 6-inch lines. The Garberville SD recently completed a water system improvement project that included: new submersible river intake pumps and emergency power supply; a new surface water treatment plant with new pressure filters, highly efficient chlorine contact chamber, and a backwash water recycling system; the retrofit of an existing booster pump station with new pumps, valving, and controls; over one mile of new water mains and distribution piping; and a new 750,000 gallon finished water storage tank. In addition, the Garberville SD recently annexed 84 Assessor’s Parcels already served by the District, into the district boundary. According to the Local Agency Formation Commission (LAFCo) staff report for the annexation, “The District has been actively planning and constructing water and wastewater facility improvements to address system deficiencies and to provide sufficient capacity to meet current and future service demands.” | Fair condition/ Upgrades planned/ identified | [7 empty] | sewer | The Garberville SD wastewater system consists of a collection system with lift stations to convey wastewater to a central treatment facility. In 2011, the District completed a major treatment plant upgrade to address capacity limitation and a RWQCB cease and desist order. The $3.5 million project included: three oxidation ponds, four wetland treatment ponds, chlorination via an onsite chlorine generation system, improved percolation ponds, and an onsite operation and maintenance building. The first primary oxidation pond was constructed at a new location. The other oxidation ponds and the wetland treatment ponds were created by modifying the existing treatment ponds and recharge basin. Improvements to the percolation ponds consisted of cleaning and re-grading each basin. In November 2011, the Water Quality Control Board rescinded the cease and desist order and issued a new Waste Discharge Permit (ID# 1B831200HUM) for the treatment plant. This waste discharge permit contains guidelines for an average dry weather flow of 162,000 gpd and a peak wet weather flow of 235,000 gpd. The treatment plant is currently operating at 38.88% of the capacity during dry weather flows. | Good condition
y |  | GASQUET C.S.D. | 35769 |  | 1 |  | CSD | P.O. BOX 86 GASQUET, CA 95543 | y | y | y | 210 | uniform rate schedule | Familiar; infrequent participation | Unfunded | 3 | 2 | 3 | 1 | 3 | 3 | 2 | 1 | 0 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | Gasquet, CA | Del Norte | North Coast, Region 1 | n | 775 | SW | Instream - North Fork Smith River |  |  | 0-50 | $0 - $50 | Raw water is pumped by the Gasquet CSD from the Smith River to a water treatment plant located approximately 500 feet from the river. Upon treatment, the water enters into a distribution system comprised of 6-inch, 8-inch and 4-inch mainlines, which has metered connections. There are two storage tanks, which total 350,000 gallons of storage.The Gasquet CSD’s existing water system, originally constructed in the late 1960s, has been modified somewhat over the years. The water system includes the following infrastructure:oTwo 5 horsepower (hp) submersible pumps; oTwo 3 hp submersible pumps; o6-inch, 8-inch,and 4-inch water distribution line throughout service area;oTwo storage tanks (150,000 and 200,000 gallons); andoWater Treatment Plant:-Two adsorption clarifiers; -Four 5,000 gallon contact tanks; -6,000 gallon “old” adsorption clarifier (serves as a contact tank);-Two 1,200 gallon “wet well” tanks;-Four booster pumps (7.5 hp, 10 hp, 15 hp, and 20 hp); and-Pressure and sand filter. | The District receives surface water from the Smith River at the confluence of the North Fork and Middle Fork. The District holds a Water Rights Permit to take up to 345 gallons per minute (gpm), with an annual withdraw limit of 135.9 million gallons (417 acre-feet). Raw water is pumped by the Gasquet CSD from the Smith River to a water treatment plant located approximately 500 feet from the river. Upon treatment, the water enters into a distribution system comprised of 6-inch, 8-inch and 4-inch mainlines, which has metered connections. There are two storage tanks, which total 350,000 gallons of storage.The Gasquet CSD’s existing water system, originally constructed in the late 1960s, has been modified somewhat over the years. The existing water delivery system is adequate to serve the Gasquet community. As water demand grows, the water treatment system is approaching its treatment capacity. Capacity challenges were documented in the District’s 2009 Water Treatment Plant Capacity Report and are summarized above. Some of the WTPCR recommendations have been implemented; other portions are currently being, or are scheduled for, implementation. Replacements and upgrades occur as needed. The District did not identify any immediate infrastructure needs at this time. | Adequate | [7 empty] | septic | about 352 households and one commercial | Adequate
|  | GEYSERVILLE SANITATION ZONE | 46250 | 1 |  |  | Public Utility | 155 HAMILTON LANE, GEYSERVILLE, CA (Mailing:) 404 Aviation Blvd., Santa Rosa, CA 95403 | [19 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | The Geyserville Sanitation Zone (Geyserville SZ) service area covers approximately 177 acres.Physical address, 155 Hamilton Lane, Geyserville, APN 140-080-022.The Geyserville SZ provides service to approximately 318 parcels using a gravity collection system and treats wastewater from approximately 405 ESDs. | Sonoma | North Coast, Region 1 | n | 862 | [16 empty] | sewer
|  | GILL CREEK MUTUAL WATER COMPANY | 46250 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
y | y | GRENADA SANITARY DISTRICT | 43523 | 1 |  |  | Sanitary Dist | P.O. Box 415 GRENADA, CA 96038 | y | y | y | 103 | Monthly/ annual flat rate; Increasing block (graduated) rate schedule | Unfamiliar; disinterested |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Grenada, CA | Siskiyou | North Coast, Region 1 | n | 280 | GW | Well (1) | 1 |  | 51-100 | $51 - $100 |  |  |  |  | 0 | 1. Failure to collect repeat and raw source coliform bacteria samples. | 2. 9/6/17 |  |  |  | sewer
|  | Gualala Community Services District | 40185 | 1 |  |  | CSD | 8851 California Hwy 1, Gualala, CA 95445 | y |  |  | 428 | graduated | [22 empty] | Gualala, CA | Mendocino | North Coast, Region 1 | n | 750 | [17 empty] | The District provides collection, treatment, and disposal of wastewater generated by hookups within the service area and maintenance of related facilities and equipment services. Wastewater is treated to a tertiary level. To achieve the tertiary level of treatment, the District utilizes an extended aeration activated sludge plant with clarification and Title 22 Sand Filter and Disinfection method. The Wastewater Treatment Plant is a Step System. The waste solids are disposed of at a solids disposal site and the treated effluent is used to irrigate the Sea Ranch Golf Links. Using GCSD’s reclaimed water at the golf course is beneficial because the North Coast Regional Water Quality Control Board (RWQCB) indicates that wastewater effluent cannot be discharged directly to a ditch, creek, or stream. This is to protect sensitive natural resources within these types of drainages. Wastewater is collected within the GCSD boundaries in Mendocino County and transported for treatment at the District’s facility, which is located in Sonoma County. Each parcel has its own interceptor tank. Heavy rain in the area required a design for extended effluent storage during the winter season. The State Water Resources Control Board (SWRCB) took particular interest, and recommended that the plant be located in Sonoma County partially as a reclamation facility for the Sea Ranch development and golf course. Authorities felt that this recommendation would reduce and offset freshwater demands on the environmentally sensitive Gualala River. The wastewater system was designed to serve existing development and provide for additional growth within the GCSD Sewer Assessment District boundaries. All new development within Zones 1 and 2 must connect to the wastewater treatment system. The GCSD owns 15.47 acres of land on which the treatment plant is located. The parcel is located in Sonoma County (Assessor’s parcel number 122-040-010) and contains the wastewater treatment plant, a maintenance garage, office trailer, and lab. | Good condition
| y | HAPPY CAMP C.S.D. | 41000 | 1 |  |  | CSD | P.O. BOX 1129 HAPPY CAMP, CA 96039 |  | y |  | 453 | Uniform Rate Schedule | Familiar; infrequent participation | Funded | [10 empty] | 1 |  |  | 1 | 1 |  | 1 | 1 |  |  | Happy Camp, CA | Siskiyou | North Coast, Region 1 | n | 1100 | SW | Instream - Elk Creek |  |  | 0-50 | $0 - $50
| y | HAPPY CAMP S.D. | 41000 | 1 |  |  | Sanitary Dist | P O Box 379 HAPPY CAMP, CA 96039 |  | y |  |  | Uniform Rate Schedule | Familiar; infrequent participation | Funded | [10 empty] | 1 |  |  | 1 | 1 |  | 1 | 1 |  |  |  | Siskiyou | North Coast, Region 1 | n | [5 empty] | 0-50 | $0 - $50
|  | HEIGHTS MUTUAL WATER COMPANY | 42958 | 1 |  |  | Mutual | PO. BOX 58 FULTON, CA 95439 |  |  |  | 110 | [24 empty] | Sonoma | North Coast, Region 1 | n | 363 | GW | Well (3)
y | y | HILLS RANCH MUTUAL WATER COMPANY | 39667 | 1 |  |  | Mutual | P.O. BOX 411 ALBION, CA 95410 | n | n | n | 48 | Monthly/ annual flat rate, Increasing block (graduated) rate schedule, tiered for water useage | Familiar; lack resources to participate |  | 1 | 1 | 1 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | Hills Ranch Road, Mendocino, CA | Mendocino | North Coast, Region 1 | n | 60 | GW | Wells (4) |  |  | Average service fees range between $81 and $100 per month. | $51 - $100 | The Company owns and maintains 4active wells and approximately 2miles of pipeline, a 200,000 gallontank,and 3chemical feed pumps. The Fire District owns a tank of 100,000 gallons capacity,which is operated by the Company as an integral part of its water supply system. In additionto providing waterto the Fire Districtfor fire protection the Company has in thepastsupported the school district when their water supply failed andthe Town of Mendocino during a period of severe drought. | In 2014 the Company was placed under the groundwater use regulations of Mendocino City Community Services District (MCCSD), which are susceptible to restrictions during time of droughts. The Company is exploring reactivation of its surface water sources in Slaughterhouse Creek as a means of resolution to the issue. A connection with the Surfwood Mutual Water Corporation is another possibility the Company is considering, as is a connection to a potential citywide water supply system should MCCSD undertake to develop one. Further challenges noted by the Company include improving water quality, upgrading their plant, installing an additional fire hydrant, responding to disasters such as earthquakes, and replacing tanks. | Poor condition | Excessive storage, some customer complaints about water quality and taste | [10 empty] | 1
|  | HILTON MUTUAL WATER COMPANY | 49732 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
| y | HOLLAND HEIGHTS MUTUAL WATER COMPANY | 46037 | 1 |  |  | Mutual |  | n | n |  | 100-250 | Increasing Block (Graduated) Rate Schedule | Unfamiliar; disinterested | [6 empty] | 1 | [5 empty] | 1 |  | 1 | [5 empty] | 1 | We serve the Holland Heights Neighborhood, adjacent to Santa Rosa in Sonoma County | Sonoma | North Coast, Region 1 | n | 250-500 |  |  |  |  | $0-50 | $0 - $50
y | y | HOLLY RANCH VILLAGE | 39667 | 1 |  |  | other | 32400 Creekside Lane, Fort Bragg, CA 95437 | y | n | y | 13 | monthly/ annual flat rate | Familiar; lack resources to participate |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 33300 Lassen Road, Fort Bragg, CA | Mendocino | North Coast, Region 1 | n | 50 | GW | Wells (2) |  |  | part of rent
y | y | HOPLAND PUBLIC UTILITY DISTRICT | 19356 |  | 1 |  | PUD | 151 LAWS AVENUE UKIAH, CA 95482 | n | n | y | 350 | Uniform rate schedule | Familiar; infrequent participation | Unfunded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | Hopland, CA | Mendocino | North Coast, Region 1 | n | 1069 | GW | Wells (2) |  |  | 100-150 | $101 - $150 |  | The HPUD serves 350 water customers but has no water rights. The HPUD maintains two storage tanks with a capacity of 800,000 gallons, which is approximately half the summer supply. Current demand is 350 AFY. The HPUD contracts with RRFC for up to 400 AF of Lake Mendocino water. The HPUD has sufficient water capacity. The Ukiah Valley Special Districts Municipal Service Review of 2013 recommended that Willow CWD, Calpella CWD, and Hopland PUD consider a formal consolidations through LAFCO. | Adequate | [7 empty] | sewer | [5 empty] | 1
|  | HORNBROOK C.S.D. | 33000 |  | 1 |  | CSD | P.O. Box 29 HORNBROOK, CA 96044 |  |  |  | 147 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 280 | SW | Instream plus wells (3) | [8 empty] | 0 | 1. Failure to conduct routine monitoring for coliform bacteria in drinking water | 1. 1/20/2016
| y | Hussey Ranch Corporation (HRC) C.S.D. | 26544 |  | 1 |  | CSD | 159 CLUB DRIVE CRESCENT CITY, CA 95531 | no | n |  | 51 | Monthly/ Annual Flat Rate | Familiar; not a participant | [21 empty] | Some unincorporated areas of Del Norte County. | Del Norte | North Coast, Region 1 | n | 150 | GW | Well |  |  | 30 | $0 - $50 |  | The HRC CSD gets its water from a well on Peacock Ranch, located adjacent to the Smith River, which provides water to residential users and the Del Norte Golf Course. The State Department of Health Services classifies the HRC CSD’s source water as groundwater. The classification of water source type dictates the water system regulations to ensure water quality. The district has a 132,000 gallon storage tank and distribution piping. The system has a maximum capacity of approximately 100 connections. The HRC CSD’s overall water system is in good condition. The existing system has no major deficiencies for serving the current population. Due to age and composition the existing poly piping serving homes around the golf course is in need of replacement and should be scheduled. In addition to the Peacock Ranch operation, two small privately owned water systems are in use. The Kelsey Trail Water Company, located in the northeast corner of the HRC CSD SOI between North Bank Road and the Smith River, serves residential users. The second privately ownedsystem, Blackberry Water Company, located in the southern portion of the HRC CSD SOI between North Bank Road and Smith River, serves the immediately surrounding residential area.The Jedediah Smith Homeowners Association (JSHOA) board members and residents have inquired about connecting their water system with the HRC CSD. The JS HOA is located just north of the district boundaries and in the sphere of influence. The HRCCSD responded that if the JSHOA is willing to provide additional infrastructure needed to compensate for the new system demand a connection could be considered. HRCCSD requested that JSHOA get an independent evaluation to address technical issues in each system. | Adequate
y |  | HUCKLEBERRY MUTUAL WATER COMPANY | 35000 |  | 1 |  | Mutual | 5514 Doyle Street EMERYVILLE, CA 94608 | y | y | n | 29 | monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 0 | 3 | 3 | 3 | 3 | 0 | 1 | 2 | 0 | 3 | 2 | 1 | 2 | 3 | 1 | 1 | 1 | 2 | 3 |  | Huckleberry Community in Cazadero, CA | Sonoma | North Coast, Region 1 | n | 45 | GW | Well |  |  | 51-100 | $51 - $100 |  |  |  |  | A | 1. Total coliform MCL violation for August 2013 | 1. 9/30/13 | [7 empty] | 1
y | y | HUMBOLDT BAY MWD | 20346 |  | 1 |  | Municipal Water Dist | Municipal Water Dist | y | y | y | 209 | Increasing block (graduated) rate schedule | Familiar; regular participant | Funded | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | greater Humboldt Bay area - including the cities of Eureka, Arcata and Blue Lake, as well as Community Service Districts serving unincorporated areas such as McKinleyville, Cutten, Fairhaven, Fieldbrook and Manila. The population served via these agencies totals about 65,000 people. | Humboldt | North Coast, Region 1 | n | 65000 | GW | Wells (5) |  |  | 0-50 | $0 - $50 | Drinking water delivered by the district is drawn from wells located in the bed of the Mad River northeast of Arcata. These Ranney Wells, draw water from the sands and gravel of the riverbed at depths of 60 to 90 feet, thereby providing a natural filtration process. In the summer this naturally filtered water is disinfected with chlorine and delivered to the District’s wholesale municipal and retail customers in the Humboldt Bay Area. In the winter the water is further treated at a regional Turbidity Reduction Facility which reduces the occasional turbidity (cloudiness) in the District’s source water. The District’s source water has been classified by the DHS as groundwater. A groundwater classification dictates the regulations that a water system must follow to ensure water quality. | [7 empty] | 1. Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Woodley Island Marina, WDID NO. 1 12I019820 2. Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Redwood Terminal 2, SCDC No. 1 12I025990 3. Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Fields Landing Boat Yard, WDID No. 1 12I019819 4. 2nd Noncompliance: Failure to submit 2015-2016 Annual Report as required by the General Permit for Storm Water Discharges Associated with Industrial Activities, Fields Landing Boat Yard, WDID No. 1 12I019819 5. Water Quality Certification For HBMWD - Mad River Operations 6. Water Quality Certification for HBMWD - RW Mathews Dam/ Ruth Lake Operations | 1. 8/4/16 2. 8/4/16 3. 8/4/16 4. 9/12/16 5. 9/15/15 6. 9/15/15
y | y | HUMBOLDT C.S.D. | 44257 | 1 |  |  | CSD | Humboldt CSD P.O. Box 158 CUTTEN, CA 95534 | y | y | y | 7714 | uniform rate schedule | Familiar; lack resources to participate | Unfunded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 0 | 2 | 3 | 2 | Outside Eureka City limits | Humboldt | North Coast, Region 1 | n | 22842 | GW | CC - Humboldt Bay MSD - Purchased, wells (2) |  |  | 51-100 | $51 - $100 | Water for the Humboldt CSD system is provided by the Humboldt Bay Municipal Water District (HBMWD) and three wells located in the Humboldt Hill area. HBMWD has sufficient water supply to meet the demands of Humboldt CSD and its other municipal customers, and Humboldt CSD has extensive available capacity within District wells. | There are no significant deficiencies within Humboldt CSD’s water system, although some storage and fire flow improvements are anticipated. Water service within Humboldt CSD is generally very good. The District purchases approximately 33% of its potable water from the Humboldt Bay Municipal Water District. 34% of the district’s water is provided from District owned wells located at the base of Humboldt Hill and Spruce Point area. These wells primarily serve Humboldt Hill, Fields Landing, King Salmon, College of the Redwoods, and some portions of the Pine Hill area. The Humboldt CSD UWMP indicates that water depths in the wells (installed in 1988) are not influenced by climatic variation and not susceptible to drought conditions (Humboldt CSD UWMP 2015, Page 14). The District also has a long term contract with the City of Eureka to purchase additional water (34% of total demand), which also originates from Humboldt Bay Municipal Water District. The district and City’s water systems are interconnected at various locations allowing for such transfers to occur. Humboldt CSD supplies water to 7,698 active connections (HCSD 2015 SWRCB Annual Report), approximately 97% of which are residential. Humboldt CSD’s water system in Freshwater is in good condition overall. There are no major infrastructure deficiencies associated with the existing system. Water service within Humboldt Hill is generally very good. The District has an ongoing program for upsizing undersized water mains installed to improve fire protection. Myrtletown’s water system is in good condition overall. There are no major infrastructure deficiencies associated with the existing system. Humboldt CSD is replacing older steel pipe in the distribution system as funding is available. Humboldt CSD’s South Eureka water system is in good condition overall. There are no major infrastructure deficiencies associated with the existing water system. Some older steel pipe in the distribution system is currently being replaced and additional water storage capacity is planned to support planned growth and improve fire protection. | Fair condition/ Upgrades planned/ identified | [7 empty] | sewer | Humboldt CSD operates a wastewater collection system that interconnects with the City of Eureka collection system and the City’s Elk River Wastewater Treatment Plant (WWTP). Portions of the Humboldt CSD and City of Eureka collection systems experience inflow and infiltration (I&I) of rainwater and are near or at capacity in a number of locations during significant rain events. Although extreme wet weather flows approach the design capacity of the WWTP, the plant is designed to treat all flows that the collection system conveys in its current configuration and with the current peaking factor. The City is conducting a study of the Elk River WWTP infrastructure to identify hydraulic and process “bottlenecks” and proposes cost effective improvements to increase capacity, rather than construct a total plant expansion. The City expects that this strategy will allow step-wise increases in WWTP capacity that keep pace with development within the Humboldt CSD and the City of Eureka over the next 20 years. The City of Eureka and Humboldt CSD cooperatively worked on the Martin Slough Interceptor Project to address the collection system capacity issues. The Martin Slough project is multipurpose in function, including reducing wastewater overflows that degrade the environment, eliminating existing City and Humboldt CSD wastewater lift stations (by conversion to gravity service), improve energy conservation, and provide capacity for planned development. The Martin Slough Interceptor was put in service in November of 2014. The Martin Slough project boundaries include areas within the City of Eureka that will gravity flow into the proposed interceptor, and portions of the unincorporated area surrounding Eureka that can utilize the interceptor based on proximity and topography located within the urban limit line established by the Eureka Community Plan and the Humboldt Bay Area Plan. Portions of the South Eureka area which include Bayview, Pine Hill, Rosewood, Cutten and Ridgewood are not within the Martin Slough project boundaries. Wastewater within these areas drains to portions of the City of Eureka collection system other than the Martin Slough Interceptor. | Fair condition/ Upgrades planned/ identified
|  | Humboldt County RID #1, Shelter Cove POTW | 42118 | 1 |  |  | Resort Imp Dist | 9126 Shelter Cove Drive, Shelter Cove, CA |  |  |  | 620 | [24 empty] | Humboldt | North Coast, Region 1 | n | 1500 | SW | Instream - Telegraph Creek - raw, SP - springs - raw, wells (17)
y | y | HUNTER VALLEY CSD | 27200 |  | 1 |  | CSD | 25 Del Ponte Drive, Klamath, CA 95548 | n | N | Y | 65 | monthly/ annual flat rate | Familiar; infrequent participation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Hunter Creek Sub-division, Klamath, CA | Del Norte | North Coast, Region 1 | n | 178 | GW | Well (1) |  |  | $16 per month billed annually | $0 - $50 | Hunter Valley Community Services District supplies clear, sanitary, tasteless and odorless drinking water to 64 member customers with a capacity for a total of 80 properties within the HVCSD Jurisdiction at 50 to 60 PSI. The District sanitizes the water system once per month with chlorine using a drip monitor. | HVCSD’s water source is a single well located adjacent to Hunter Creek. Total District water use is metered, however individual residential connections are not. Water is supplied to homes through 1” PVC supply lines on an unlimited basis. HVCSD’s water system is operating at 85% of its service capacity. The water system adequately serves the existing connections with no major deficiencies, however, the system is operating near its capacity. Also, in light of current statewide drought conditions HVCSD should consider metering all connections within the District. | Fair condition/ Upgrades planned/ identified | [7 empty] | septic | all residents on own septic | Adequate
y | y | INDIAN CREEK TRAILER PARK | 50313 | 1 |  |  | Other | P.O. BOX 8 DOUGLAS CITY, CA 96024 | y | y | y | 35 | monthly/ annual flat rate |  |  | 2 | 1 | n/a | 0 | 3 | 3 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 0 | 1 | 0 | 3 | 1 | 59680 Hwy 299 west Douglas City, CA 96024 | Trinity | North Coast, Region 1 | n | 121 | SW | Instream - Indian Creek Infiltration Gallery |  |  | 0-50 | $0 - $50 |  |  |  | coliform and e coli according to the LT2 sampling. Some possible pesticides from marijuana growers up stream.** We do not detect any of these after water is through the treatment plant. | 0 | 1. Citation for failure to submit surface water treatment monthly monitoring reports | 1. 3/1/2017 |  |  |  | septic | Septic system with no treatment | Adequate
|  | IRISH BEACH WATER DISTRICT | 48828 | 1 |  |  | Water Dist | P.O. Box 67 MANCHESTER, CA 95459 15401 Forest View Road, Manchester, CA 95459 | y |  |  | 201 |  | Unfamiliar; lack resources to investigate/participate | [21 empty] | Irish Beach | Mendocino | North Coast, Region 1 | n | 560 | SW | Instream Irish Gulch Lower Intake, Upper intake, wells (2) | [5 empty] | The District has five water tanks strategically located throughout the District (Refer to Figure 5-5). Tank 3 is an 84,000 gallon tank that supplies water to the eastern side of the subdivision and was replaced in 2010. The western side of the subdivision is supplied via Tank 1, which is a 210,000 gallon tank that was replaced in 2013. A 10,000 gallon settling tank is located between the Irish Gulch diversion and treatment facility, which has a design capacity of 42 gpm (0.09 cfs) or 57 gpm (0.127 cfs) with a filter unit kept in reserve.In the 2010–2011, the lower diversion at Irish Gulch was put online, numerous fire hydrants were added throughout the subdivision, water treatment modifications were made, a transfer station was rebuilt, and a pressure reducing station was installed. The District has five water storage facilities, a pipeline network, hydrant system, and a water treatment plant. (Refer to Figure 5-5). The District has approximately 7.6 miles of pipeline, ranging from 6 to 2 inches in diameter. Parts of the District’s distribution system dates from 1965, with sections added over the years, the newest of which was installed in 2000. Over 83 percent of the District’s distribution and transmission system is more than 30 years old. Much of this system has an estimated useful life of 40 years. To address aging infrastructure needs, a Proposition 218 Assessment was passed by District voters in early the 2000s.The assessment funds are kept in a special reserve account specifically for capital improvements including but not limited to replacement of pipelines, pumps, valves, tanks, hydrants, and connections. The District faces a number of challenges including ongoing litigation and identification and development of water sources for future development. Although not an immediate need, the District will need to identify additional sources to provide water supply as buildout of the District nears. Additionally, aging infrastructure is reaching the end of its lifespan and will need to be replaced or repaired in the near future. | Fair condition/ Upgrades planned/ identified | [7 empty] | septic | In 1980 the IBWD passed a Resolution of Intention to form a wastewater disposal zone under Health and Safety Code Sections 6955, et seq. The purpose of the establishment of the zone was to monitor, the maintainance, repair, replacement and pumping of wastewater disposal systems after such systems are initially installed pursuant to County Health and/or Regional Water Quality Control Board permits and standards on properties previously established as building sites within the subdivision known as Irish Beach. The District was not required to go through LAFCo to initiate the zone. As such, the District is responsible for maintaining individual wastewater disposal system records, including date of installation, as-built plans of installed systems and service records of systems. It is also under the purview of the District to send to new owners and owners of new systems information regarding maintenance practices that should be followed and local contractors that provide service. To enforce this, IBWD passed Resolution No. 93-5, which requires that all septic tanks be inspected and/or pumped if necessary every five years by a registered sanitarian or a septic tank operator. In 2011, the District passed Resolution No. 2011-2 to establish discharge limits of waste that may contaminate the waters of the state flowing through Irish Beach. | Adequate
|  | JACOBY CREEK CSD - combined with City of Arcata | 28277 |  | 1 |  | CSD | City of Arcata 736 F Street ARCATA, CA 95521 |  |  |  | 325 | [24 empty] | Humboldt | North Coast, Region 1 | n | 913 | GWP | HB MWD purchased | [5 empty] | The Jacoby Creek County Water District is located adjacent to the south-eastern boundary of the City of Arcata and extends along Jacoby Creek in a generally south-east direction for approximately four (4) miles. The present boundaries of the District contain approximately five (5) square miles or 3200 acres. The District's water distribution system was constructed in 1974 with funds obtained from a Davis-Grunsky loan from the State of California. The District obtains its water from the City of Arcata, who in turn, obtain their supply from the Humboldt Bay Municipal Water District. An agreement with the City of Arcata provides for the City to supply water, operate and maintain the distribution system and provide billing and collection services for the District. Water service is currently supplied to 215 connections within the District. Most of these connections are for residential users plus a few small businesses. Jacoby Creek’s water system is in good condition. The biggest deficiency with the existing system is lack of adequate storage capacity. The study area has only about 27% of maximum day demand in storage capacity (Winzler and Kelly, 2008). In addition, some distribution piping within the system is fewer than six inches in diameter and unable to provide adequate fire flows. | Storage capacity insufficient
y | y | JED SMITH HOMEOWNERS ASSN. | 26544 |  | 1 |  | Mutual | 1600 TOLOWA ROAD CRESCENT CITY, CA 95531 | y | y | n | 27 | uniform rate schedule | Unfamiliar; disinterested |  | 3 | 2 | 1 | 0 | 3 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 3 | 0 | 0 | 2 | 1 | 3 | 3 | Jed Smith Homeowners' Association | Del Norte | North Coast, Region 1 | n | 58 | GW | Wells (2) |  |  | 51-100 | $51 - $100 |  |  |  | Intermittent E-coli and choliform positive testing results | B | Groundwater under Direct influence of surface water with inadequate treatment | 2017-02-17 | [7 empty] | 1
|  | JUNIPER CREEK ESTATES | 45365 | 1 |  |  | Other | P.O. Box 1108 FORT JONES, CA 96032 |  |  |  | 52 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 130 | GW | Well
|  | KLAMATH C.S.D. (Del Norte Community Development) | 27200 |  | 1 |  | CSD | P. O. BOX 430 KLAMATH, CA 95548 | y |  |  | 62 | increasing block | [22 empty] | Klamath | Del Norte | North Coast, Region 1 | n | 240 | GW | Wells (3) |  |  | 36/month water; 18.40/ month, sewer | $51 - $100 |  | The Klamath CSD water infrastructure includes three active untreated wells, one 125,000 gallon water storage tank, and a water distribution system. Water is metered and supplied to homes through 3/4” supply lines. The Klamath CSD serves approximately 62 water connections within the District. In 2014 the District hooked up three new commercial facilities to the water system including a hotel/casino, a Yurok Knowledge and Cultural Park, and the Yurok Tribe Justice Center. The water system was designed to meet both domestic water and fire flow requirements. The Klamath CSD’s water system adequately serves the existing connections with no major deficiencies. | Adequate | [7 empty] | sewer | The Klamath CSD is responsible for collection, treatment, and disposal of the community’s wastewater. The present service area consists of commercial and residential areas within the Klamath CSD. The District provides approximately 37 residential and 12 commercial wastewater service connections as of 2015. These numbers have not changed due to a Cease and Desist Order that has been placed on the wastewater system by the North Coast Regional Water Quality Control Board (NCRWQCB) since 2006. The wastewater system is capable of serving a maximum capacity of 49 connections. Existing facilities consist of a gravity collection system and transmission lines including two pumping stations, a package type contact stabilization treatment facility, and a system of leachfields. The wastewater collection system includes 3,000 feet of 8-inch and 1,950 feet of 6-inch Vitrified Clay Pipe (VCP); 10 manholes; two 200 gallon per minute (GPM) lift station pumps and vault; chambered septic tank; two 50 GPM effluent pumps; and sewer forcemain (Yurok Tribe, 2012). The existing wastewater leachfields are located directly west of the Klamath community and U.S. Highway 101, and directly east and in the vicinity of the Klamath River. The leachfield system is on Del Norte County land leased to Klamath CSD for wastewater disposal and is under the jurisdiction of the NCRWQCB. The NCRWQCB will not allow expansion of the system beyond the existing wastewater flows due to its location in the 100-year floodplain. The District is currently working on an engineering plan which will address this issue. The old sewer forcemain was located directly adjacent to the wastewater treatment facility and on the west (wet) side of Hwy 101 was temporarily replaced after 2006 storms and Klamath River flooding washed it out. In 2012, 900 feet of new 4-in HDPE sewer forcemain was installed on the east (dry) side of Hwy 101 and crossing to the west side of the highway in the vicinity of the leachfield system, removing the threat of damage to the forcemain from the Klamath River. Two new leachfields were installed in 2009 to replace leachfield capacity lost to the Klamath River in 2006, one was replaced via Indian Health Services (IHS) funding while the other was replaced via Klamath CSD FEMA funding. Two new effluent pumps and new pump chamber were constructed in 2015 to bring the wastewater system and current operation into compliance with the NCRWQCB. The overall condition of the wastewater collection piping is good according to an Inflow and Infiltration (I/I) Study completed by Graysky Engineering for Klamath CSD in 2009. Average wastewater flows throughout the year are 15,192 gallons per day (GPD) with a range of between 11,500-20,000 GPD. | Good condition
y |  | LAKE SHASTINA C.S.D | 18125 |  | 1 |  | CSD | 16320 EVERHART DRIVE WEED, CA 96094 | y | y | y | 1272 | monthly/ annual flat rate | Familiar; not a participant |  | 0 | 0 | 0 | 0 | n/a | n/a | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | Lake Shastina Community in Weed, CA | Siskiyou | North Coast, Region 1 | n | 2400 | GW | Wells (3) |  |  | 51-100 | $51 - $100 | [10 empty] | sewer | Due to the varied topography of the Lake Shastina area, most of the District is serviced by Sewer Lift Stations which pump to the plant; sewer is 36 a month for improved lots and 3 a month of unimproved | Adequate |  |  |  | 1
y | y | LAYTONVILLE COUNTY WATER DISTRICT | 23315 |  | 1 |  | Water Dist | P.O. BOX 32 LAYTONVILLE, CA 95454 | y | n | y | 397 | uniform rate schedule | Unfamiliar; disinterested |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Laytonville, CA | Mendocino | North Coast, Region 1 | n | 1320 | GW | Wells (2) |  |  | 51-100 | $51 - $100 | Coagulation/oxydation to treat arsenic The water treatment process includes oxidation with chlorine via a reaction tank, processing through filter pumps, and the addition of various coagulants and sodium bisulfite to reduce chlorine residue. Treatment with the new arsenic filtration components is also performed. After treatment, water is moved to the distribution system, which includes four storage tanks that connect to the water mains. | LCWD is operated via two separate pressure or distribution zones (the East Zone and the West Zone). The East Zone lies east of Ten Mile Creek, and includes the downtown area of Laytonville, the Laytonville K-12 school facilities, and surrounding areas along a two-mile-plus stretch of Highway 101. The West Zone, where approximately 60 percent of District customers reside, lies west of Ten Mile Creek, and includes the Cahto Indian Rancheria and Casino, as well as adjacent residential neighborhoods located on or adjacent to Branscomb Road. There are approximately 13 miles of water mains that carry water to 2 separate pressure or distribution zones (the East Zone and the West Zone) as shown in Figures 6-11 and 6-12. The East Zone lies east of Ten Mile Creek and includes two storage tanks that have a combined capacity of 750,000 gallons. The West Zone lies west of Ten Mile Creek and has two storage tanks with a combined capacity of 310,000 gallons. All four tanks, with a combined capacity of 1,060,000 gallons, are filled through the distribution system. | Good condition | Water quality is an important component of water supply. LCWD reports that water quality is currently very good and it has worked diligently to resolve past water quality issues. For the purposes of transparency, those past water quality issues are summarized here. The U. S. Geologic Survey in 1986 reported that chemical quality of water in basement rocks and valley fill is generally acceptable for most uses. Some wells may have naturally occurring high iron, arsenic, or manganese levels. The Environmental Working Group reported in 2009 that levels of manganese and arsenic exceeded adopted health limits. Additionally other constituents including total haloacetic acids, total trihalomethanes, dibromochloromethane, bromodichloromethane, bromoform, chloroform, alpha particle activity, dichloracetic acid, and radium 228 were noted. Some of these constituents are byproducts of water treatment and distribution and the District received violation notices from the State Department of Public Health CDPH) i n 2006 and 2008. The District has refined its practices to reduce byproducts and is now in compliance with standards for these constituents. The District also treats its water to lower the levels of naturally-occurring iron, manganese, and arsenic in the system. Iron and manganese in treated water do not pose a health hazard; however, arsenic in well water is a human health hazard. When the arsenic standard was lowered to 0.010 milligrams per liter in January 2006, the District was out of compliance and received notice of violation from the CDPH in 2006. The new arsenic treatment system was installed in 2008 and successfully operated in 2009. The District continues to monitor this constituent to ensure compliance with regulatory standards. In December 2009, the District updated its permit application with the CDPH to acknowledge the installation of its new arsenic treatment plant. However, those Valley residents who live outside the District boundaries and utilize their own private water wells as their primary drinking water supply do not benefit from the District’s water treatment process and remain at risk of exposure to arsenic. This is an issue that may need to be addressed with the County Environmental Health Department. A related water quality issue is the presence of hundreds of septic tanks near the ground surface and above the aquifer. Since the community of Laytonville does not have access to a formal centralized wastewater treatment system, septic tanks serve as the primary treatment and disposal method. Sometimes aging septic tanks can fail and create water quality problems such as E coli contamination. Mendocino County is aware of the issues and the Council of Governments (MCOG) and Municipal Council have developed a community plan for Laytonville to start discussing solutions.Protecting water quality is important to LCWD and it has conducted an assessment of Well 1 called a Drinking Water Source Assessment and Protection (DWSAP) Program, as managed by the CDPH. This Assessment found that a potential source of contamination for Well 1 is the rodeo restroom leach field, located adjacent to the WTP. The closed Well 2 also represents a potential source of contamination to Well 1. The District has not yet conducted a Drinking Water Source Assessment and Protection Program for Well 3 and this is a to-do item for the District. | [6 empty] | septic | individual septic systems - 100s near ground surface and above aquifer which supplies LCWD | Regulatory - septic |  | 1
y |  | LEWISTON Community Services District | 30000 |  | 1 |  | CSD | P.O. BOX 101 LEWISTON, CA 96052 | y | y | n | 49 | uniform rate schedule | Familiar; regular participant | Funded | 2 | 1 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Lewiston, CA | Trinity | North Coast, Region 1 | n | 250 | SW | New downstream intake (2015) - raw |  |  | On average, it's about $46/month for water and $54 for wastewater | $51 - $100 | Arsenic was a problem with prior source, but since the new WTP was constructed, it's not a problem. | [14 empty] | 1
|  | LITTLE LAKE MOBILE HOME PARK | 32667 |  | 1 |  | Other | 1500 BAECHTEL ROAD WILLITS, CA 95490 |  |  |  | 19 | [24 empty] | Mendocino | North Coast, Region 1 | n | 40 | GW | Well
y | y | LOLETA C.S.D. | 46458 | 1 |  |  | CSD | P.O. BOX 236 LOLETA, CA 95551 | y | y | y | 280 | uniform rate schedule; water: monthly fee + uniform volume rate wastewater: annual fee based on use type | Familiar; infrequent participation | Unfunded | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | Loleta, CA | Humboldt | North Coast, Region 1 | n | 750 | GW | Well (2) |  |  | water $45/mo.; wastewater: $47/mo. (569/yr: SFR) | $51 - $100 | The District operates two wells located on Peugh Road in Loleta. Water is pumped from the wells through a Green Sand filter where the iron and manganese is removed by injecting chlorine and potassium permanganate. | Treated water is provided to the service area through approximately 4.5 miles of pipe and to a 225,000 gallon storage tank located just off the freeway. The treatment system runs an average of twelve to thirteen hours a day. One of the wells located on Peugh Road pumps on the average of 60,000 gallons of water a day. Development of the other well is currently in progress. The capacity of the new well is designed to produce 309,600 gallons per day (gpd). It should be noted that most of the Loleta area generally have low yields and water quality issues. With the new well producing the designed capacity, the capacity of water production for the Loleta water system will be 369,600 gpd; this is the ideal production rate, the target water production rate is 144,000 gpd. The storage capacity of the Loleta System is 225,000 gallons, which translates to approximately 1.4 days storage (according to the peak daily usage data). A current estimation of peak usage of the system is 157,000 gpd. According to the designed water production, and including the storage capacity of the system’s 225,000 gallon tank, the Loleta water system is at 26 percent capacity on the highest use day of the year. However, these numbers do not take fire suppression in to consideration, and they are based on the assumption that the facilities are in perfect running order. The District serves 226 homes, 11 businesses, and 2 industrial sites. Due to poor water quality, the Loleta CSD received funding from USDA as well as American Recovery and Reinvestment Act funding, to construct an improvement project that included a new well, transmission line, and treatment plant. The water system improvements are on-line and are sized to serve existing development and currently planned development. According to the LAFCo Municipal Services Review (2008) “the Loleta water system is at 26 percent capacity on the highest use day of the year. However, these numbers do not take fire suppression into consideration, and they are based on the assumption that the facilities are in perfect running order. The District believes that they can supply an additional 60-70 (40 to 50 based on Building Permit data as of 2016) homes.” | Good condition | [5 empty] | Admin Civil Liability | 2018.04.24 | sewer | The District currently relies on percolation ponds for the disposal of treated effluent. This form of disposal is becoming increasingly difficult to permit due to stringent regulations governing disposal to the Eel River during the discharge prohibition period. Other communities such as Rio Dell and Ferndale are being required by the NCRWQCB to find alternative methods of disposal. The District has significant problems with I&I within their collection system, and is operating its wastewater system under a cease and desist order (R1-2015-008) due primarily to excessive I&I. The cease and desist order prohibits additional influent from new or increased connections by the Loleta CSD, except from building permits approved before March 12, 2015. Where the peaking factor has been reduced to 5.5, the Loleta CSD may request to connect additional new or expansion of existing connections provided the additional flows are off-set by a reduction of I&I by at least 2:1 to the collection system. The Loleta CSD is required to complete repairs and upgrades to the system to address this problem by 2019. The Loleta CSD submitted a notice of exemption to the State Clearing House (SCH 2016118314) in November of 2016 for a project to rehabilitate approximately 4,000 feet of sewer main, lateral connections, and a man hole to reduce peak wastewater flows and improve treatment efficiency. | Fair condition/ Upgrades planned/ identified
|  | MACDOEL WATERWORKS | 28500 |  | 1 |  |  | 630 NORTH FIFTH STREET KLAMATH FALLS, CA 97601 |  |  |  | 18 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 35 | GW | Well
| y | MADRONE MUTUAL WATER COMPANY | 50667 | 1 |  |  | Mutual |  | n | n |  | 0-25 | Monthly/ Annual Flat Rate | Unfamiliar; disinterested | [20 empty] | 1 | Cotati, CA | Sonoma | North Coast, Region 1 | n | 50-100 |  |  |  |  | $0-50 | $0 - $50
|  | MAGIC MOUNTAIN MUTUAL WATER COMPANY | 37308 |  | 1 |  | Mutual | P.O. Box 566 MONTE RIO, CA 95462 |  |  |  | 67 | [24 empty] | Sonoma | North Coast, Region 1 | n | 100 | GW | Well | [8 empty] | A | 1. Total coliform MCL violation for March 2014 | 1. 5/8/14
y | y | MANILA COMMUNITY SERVICES DIST. | 38816 | 1 |  |  | CSD | 1901 PARK ST. #3 ARCATA, CA 95521 | y | y | y | 357 | monthly/ annual flat rate; Sewer is flat rate. Water is flat rate plus $/hcf | Familiar; infrequent participation |  | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | Manila, CA | Humboldt | North Coast, Region 1 | n | 1000 | GWP | CC - Humboldt Bay MWD Purchased |  |  | 75 | $51 - $100 |  | Manila’s water system is in good condition. The only major deficiencies associated with the existing system are some undersized water mains and inadequate storage capacity. The District has no major plans for system upgrades at this time. The Manila CSD is planning to carry out minor upgrades, such as replacing valves, installing new fire hydrants, and replacing the storage tank roof in the near future. The District is also applying for grants to increase water storage capacity. The District purchases its potable water from the Humboldt Bay Municipal Water District (HBMWD). Water is delivered to Manila by a 15-inch diameter main that continues south through Manila to serve the towns of Samoa and Fairhaven and the pulp mill. A 10-inch diameter main provides water to the District. The District provides water service for approximately 357 service connections (2003) consisting of 354 residential and 3 commercial/industrial. There is ample water from the supplier to meet future demands until maximum build-out of the District occurs. | Good condition | [7 empty] | sewer | The Manila CSD wastewater system is in good condition overall. The community relies on a Septic Tank Effluent Pump (STEP) system that pumps liquid effluent from septic tanks into a force main to the treatment facility. The treatment system consists of three free surface wetlands, two surface aerated facultative ponds, and four percolation ponds (rapid infiltration basins) for disposal. The system currently has approximately 444 connections, and flows currently range between 0.066 MGD during dry weather and 0.21 MGD during wet weather. The facility has an average dry weather flow design capacity of 0.14 MGD, and is operating at approximately 47% capacity. The District’s collection system and treatment system are in overall good condition. The system is in compliance with its waste discharge requirements and has sufficient capacity to serve forecasted potential future development without major improvements, although infrastructure extensions might be needed to serve a particular parcel. | Good condition
| y | MCCLOUD C.S.D. | 39083 | 1 |  |  |  | P.O. Box 640, McCloud CA 96257/ 220 W Minnesota Street | y |  |  | 728 | [8 empty] | 1 | [14 empty] | McCloud, CA | Siskiyou | North Coast, Region 1 | n | 1300 | GW | Springs (3), Intake Squaw Springs, Lower Elk Springs, Upper Elk Springs
| y | MARK WEST ACRES MWC | 46037 | 1 |  |  | Mutual |  |  | n |  | 23 | Monthly/ Annual Flat Rate | Unfamiliar; disinterested | [21 empty] | Mark West Acres, Mark West Watershed | Sonoma | North Coast, Region 1 | n | 0-50 |  |  |  |  | $0-50 | $0 - $50
| y | MARK WEST MUTUAL WATER CO. | 46037 | 1 |  |  | Mutual |  | n | [26 empty] | Mark West Meadows, Sonoma County | Sonoma | North Coast, Region 1 | n
y | y | MCKINLEYVILLE C.S.D. | 46708 | 1 |  |  | CSD | P.O. BOX 2037 MCKINLEYVILLE, CA 95519 | y | y | y | 5616 | Increasing block (graduated) rate schedule | Familiar; infrequent participation | Unfunded | N/A | 1 | 0 | 1 | N/A | N/A | 0 | 0 | N/A | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | McKinleyville, CA: Pacific Ocean to the first eastern ridge and from Mad River north to Little River | Humboldt | North Coast, Region 1 | n | 16900 | GWP | Purchase from Humboldt Bay MWD |  |  | 100-150 | $101 - $150 | purchased from HBMWD | The District’s current storage capacity for potable water is 5.25 million gallons in six storage tanks located on McCluski Hill (100,000 and 150,000 gallons), Cochran Road (1 million and 1.5 million gallons) and Norton Road (1 million and 1.5 million gallons). This can leave a 24-hour backup water supply for McKinleyville water customers at peak flow. Two new 3-million gallon tanks are also planned for construction on the District’s Murray Road site. McKinleyville CSD is in the process of determining the viability of the Murray Road tank site due to seismic considerations. A cost analysis will be conducted to determine the feasibility of design at that site opposed to purchase of a site in a less sensitive location. New tanks would increase the District's storage capacity, enhance fire flows during peak summer usage, and provide additional system capacity for new growth. McKinleyville CSD has determined it would be more advantageous to initiate phased construction of two tanks at this location to spread the cost over a longer period of time, and to enhance the operational flexibility of the system by having two tanks to allow for maintenance and redundancy. (McKinleyville CSD UWMP, Modified April, 2013.) Treated water is piped from the Essex Hill storage tank under the Mad River to the MCSD’s Grant A. Ramey Pump Station at the intersection of Azalea and North Bank Roads. The water is then boosted up to two storage tanks located at Cochran and Norton Roads and in-turn to a third higher elevation tank on McCluski Hill. This system provides a gravity-flow distribution of water to end users and fire hydrants throughout the water service area. A fourth undeveloped tank site on Murray Road has been purchased by the MCSD to serve future community water needs. The total potential system storage capacity is approximately six million gallons. The delivery system, from storage tanks to individual users, consists of about 70 miles of water mains. “McKinleyville and the City of Arcata’s water supply are vulnerable to natural disaster, therefore, an emergency intertie was constructed to allow for the flow of water to occur between both systems if necessary. This line remains stagnant when not in use, therefore, a 5/8-inch bypass was installed which allows the water within the intertie to turnover and maintain its chlorine residual. All water that passes through the bypass is metered and currently enters into the City of Arcata’s water system from the McKinleyville system.” (McKinleyville CSD UWMP, 2015: P 13) | Fair condition/ Upgrades planned/ identified |  |  |  |  | C | 1. NOV & Transmittal of the 3/13 Compliance Evaluation Inspection Report. Deficiencies include: laboratory deficiencies; not monitoring for pH and temperature daily; monitoring records not correlated with periods of discharge; O&M manual not being followed and in need of update. | 1. 4/23/13 | sewer | The McKinleyville CSD wastewater management facilities consist of two primary oxidation ponds (11.2 acres total), two secondary oxidation ponds (5.5 acres total), two finishing treatment marshes (5.6 acres total), with a total pond area of 22.3 acres. Biological treatment capacity of the ponds is 1.18 mgd (1,180,000 gallons per day) and hydraulic capacity of disinfection facilities (chlorine contact chamber) is estimated at 3.3 mgd (2300 gpm) peak flow. Treated wastewater is discharged to the Mad River during winter months when the river flow rate surpasses 200 cfs (cubic feet per second). During summer months (May 15 through September 30) and low flow periods of the Mad River, treated wastewater is discharged into two percolation ponds located adjacent to the river and is irrigated on dairy pastures in southwest McKinleyville. (McKinleyville CSD website, Wastewater Management Facility-About the Facility) The McKinleyville CSD completed a 20 Year Wastewater Facilities Plan (WFP) in January 2012, which identified a series of upgrades to the existing wastewater treatment plant, including portions of the effluent disposal system. Projected 20-year flows for year 2030 were developed based on a 1.8% annual increase in population. The projected average dry weather flow for year 2030 is 1.4 MGD and the projected average wet weather flow is 1.7 MGD. The projected peak day flow for year 2030 is 3.1 MGD. Based on the Wastewater Facilities Plan, the improvements will address the needs for the facility through the year 2030. The WFP presented several treatment alternatives and recommended replacing the existing facultative lagoon system with an in-basin extended aeration system. Subsequently, two manufacturers of in-basin extended aeration systems, Bioworks and Parkson, were chosen as the preferred vendors for the extended aeration system. The proposed Wastewater Management Facility (WWMF) improvements include a new headworks facility; aeration basins; a blower/electrical/maintenance building; two new secondary clarifiers, including return activated sludge/waste activated sludge pumping; and a biosolids storage basin. The improvement project was initiated in January 2016, and is currently under way. (McKinleyville CSD website, Wastewater Treatment Plant Upgrade, http://mckinleyvillecsd.com/wastewatermanagement-facility) | Fair condition/ Upgrades planned/ identified
y |  | MEADOW ESTATES MUTUAL | 36932 |  | 1 |  | Mutual | 13250 ESTATE DRIVE BOONVILLE, CA 95415 PO Box 64, Boonville, CA 94515 | y | y | y | 35 | Increasing block (graduated) rate schedule | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | Meadow Estates Subdivision, Boonville, CA | Mendocino | North Coast, Region 1 | n | 85 | GW | Wells (3) |  |  | 51-100 | $51 - $100 |  | The Company owns and maintains three active wells. | Adequate
|  | MELITA HEIGHTS MUTUAL WATER COMPANY | 46037 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
y | y | MENDOCINO CITY C.S.D. | 51277 |  |  | 1 | CSD | P.O. Box 1030 (10500 Kelly Street) MENDOCINO, CA 95460 | y | y | y |  | uniform rate schedule; monthly/ annual flat rate | Unfamiliar; disinterested |  | 2 | 2 | 2 | 0 | 2 | 3 | 3 | 0 | 0 | 3 | 3 | 1 | 1 | 1 | 0 | 1 | 2 | 1 | 3 | 1 | Town of Mendocino, CA , Russian Gulch State Park and Headlands State Park | Mendocino | North Coast, Region 1 | n | [5 empty] | 51-100 | $51 - $100 |  | We only have responsibility for ground water extraction. All members of the district obtain water from private wells or neighborhood private water companies. There is no central water distribution system in the district. Individual property owners receive their water from privately owned wells. The district has responsibility to monitor and control the amount of water extracted by each property owner. Groundwater is the primary water supply for the community of Mendocino; water trucked in during the summer months provides a secondary supply. Every developed parcel has a well; individual wells are used to supply both commercial and residential water use. In 1990, MCCSD adopted a Groundwater Management Plan (GMP) and Groundwater Extraction Permit Ordnance, 90-1. At the time of adoption two primary elements were included in the GMP: (1) groundwater extraction permitting procedures and; (2) mandatory water conservation requirements. Since adoption of the GMP the District has adopted additional programs to include: (1) a Voluntary Water Conservation Education Program; (2) a Groundwater Monitoring Program; (3) a Water Recycling Program; (4) a Data Management Program and; (5) a Water Shortage Contingency Plan. | Adequate | [7 empty] | sewer | The MCCSD Sewerage System is comprised of collection, treatment and disposal facilities. The District manages and maintains over 47,000 feet of collection system sewer lines and three lift stations. Since initial construction,the plant has been upgraded. In 1990 a belt filter press was added to de-water digested sludge to about 10%to 12% solids. In 2004, a dehydration unit was installed after the belt filter press to de-water sludge to Class A biosolids (greater than 90% solids and no pathogens). The Class A biosolids are transported to a sanitary landfill for final disposal.Treated effluent is discharged to a flow equalization pond which provides a constant discharge into the Pacific Ocean through a 996-foot outfall pipe. Since inception, the largest total annual flow through the system was in 2006. In that year, the total flow through the system was 45.55 million gallons; all but two million gallons weredischarged to the ocean. In 1997, the District installed a recycled water system that pumps treated effluent to the Mendocino High School to irrigate the athletic fields. This system provides about two million gallons of water per year to the High School. The District’s collection system overlies the community’s shallow unconfined aquifer. Groundwater is the primary water supply for the Mendocino community. Individual wells are used to supply both commercial and residential water use.Many of these wells are near the wastewater collection systempipes. Because of thi scircumstance, the District is very concerned about any overflows from the system and potential exfiltration to the aquifer. The District has developed a proactive operation and preventive maintenance program known as the Collection System Operation and Maintenance Program (CSOMP). (See below for additional information on this program) Based on the District’s efforts with this program, it appearsthat most of the additional flow to the plant during wet years or the wet time of the year is caused by additional water consumption and/or is caused by inflow rather than infiltration. Inflow can occur through manholes, gutter drops from houses,yard drains, lateral cleanouts orother similar kinds of connection issues on individual parcels.The district also indicates that much of the additional flow is from the unlined emergency overflow pond and drying beds. The District has also observed that much of the increased flow happens immediately after a rain event which indicates inflow rather than infiltration. | Fair condition/ Upgrades planned/ identified
|  | MENDOCINO COUNTY WATER WORKS DISTRICT NO. II | 40185 | 1 |  |  | County Dist | [29 empty] | Mendocino | North Coast, Region 1 | n
|  | MICHELE MUTUAL WATER COMPANY | 42958 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n | 170 | GW | Wells (2)
|  | MILL CREEK M.W.C. | 49403 | 1 |  |  | Mutual | P O BOX 864 FORTUNA, CA 95540 |  |  |  | 36 | [24 empty] | Humboldt | North Coast, Region 1 | n | 65 | GW | Wells (2)
|  | MILLVIEW COUNTY WATER DISTRICT | 19356 |  | 1 |  | Water Dist | 3081 NORTH STATE STREET UKIAH, CA 95482 | y |  |  | 1608 | graduated block - in addition to a meter charge, the MCWD charges a fee of $3.42 for every 1,000 gallons, which goes to O&M and capital improvements (implemented 2009) | Unfamiliar; interested | [21 empty] | Millview, CA; The MCWD serves an 8.5-square-mile service area northeast and immediately north of Ukiah city limits. | Mendocino | North Coast, Region 1 | n | 5568 | SW | Russian River Intake, Instream, Wells (3), Wells, Surface influenced (16) |  |  |  |  | The plant consists of three river intake pumps, four horizontal press filters, two clearwells, and three high-service pumps. The plant is normally used in the summer months, due to higher demands. | The MCWD receives most of its water from surface water rights. In addition, it can purchase up to 1,520 acre-feet (AF ) of Lake Mendocino water. During the period from 2000 to 2009, the MCWD was able to meet demand. The average demand from 2000 to 2008 was 1,462 AF and production was 1,556 AF. Demand for a year with normal precipitation (2004) was 1,522 AF, which is used as the baseline for projections to 2030.The MCWD has sufficient supply to serve its customers through 2015. A recent cease and desist order would reduce available supply by 785 acre-feet per year (AFY). The order is being contested; however, if it is upheld, the MCWD would have difficulty supplying water in 2020 and beyond unless it can purchase additional Lake Mendocino water or find another source. The MCWD also owns and operates a treatment plant capable of treating 2400 gallons per minute. The plant is located at 2850 Redemeyer Road (Exhibit 3.2-1 ). It has a design capacity of 3.0 million gallons per day (mgd). Average daily demand is 1.7 mgd, maximum daily demand is 2.7 mgd. The plant has sufficient capacity to meet an estimated peak demand of 2.8 mgd. The plant consists of three river intake pumps, four horizontal press filters, two clearwells, and three high-service pumps. The plant is normally used in the summer months, due to higher demands. The MCWD also owns and operates a well field located immediately adjacent to the existing water treatment plant. The well field is used to provide water through the water treatment plant and to the distribution system for a majority of the year. During the summer higher demand period, groundwater is blended with treated surface water.The MCWD has a storage capacity of 3.24 million gallons or approximately two days’ supply. The MCWD also maintains two pump stations located in the Deerwood subdivision that pump water to and from its storage facilities. The MCWD’s existing infrastructure is sufficient to meet current demand; as additional supplies are secured, the MCWD can increase treatment plant capacity and storage to meet demands of additional new services. However, with the moratorium, expansion is not contemplated in the near future. The MCWD offices have moved to 151 Laws Avenue, which houses the RRFC and WCWD, and shares office space with the staff of the Willow County Water District. This move has resulted in the cross training of office staff, field personnel and the opportunity to combine resources, reduce cost, and provide more efficient service to better serve the customers of the districts. The MCWD occasionally uses the boardroom at that location for special meetings.City of Ukiah to the south and the CCWD to the north. In addition, the MCWD treats and wheels water to CCWD. The MCWD also has a contract to purchase Lake Mendocino Water from the RRFC. | Uncertain water supply
y | y | MIRANDA C.S.D. | 33438 |  | 1 |  | CSD | P.O. BOX 160 MIRANDA, CA 95553 | y | y | y | 142 | uniform rate schedule | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 0 | Miranda, CA within the District boundaries | Humboldt | North Coast, Region 1 | n | 600 | GW | Wells (2) |  |  | 0-50; Sewer - $23 monthly, water $12.00 monthly for basic - extra charges for more than 1200 cubic feet. The District is in the process of determining how much to raise the rates, which should be completed this year. | $0 - $50 | The pumps are operated in a lead lag arrangement, with the larger pump leading during summer months and the smaller pump leading during winter months. There are 6-inch asbestos cement (AC) and ductile iron pipes from the wells to the treatment building. Continuous disinfection is provided through a BIF metering pump that injects calcium hypochlorite into the main line. The meter is switched on by the well pumps. Soda ash is used to raise the pH of the water, which is typically around 6.1. | The District’s water source is two wells with a total capacity of 0.338 MGD. The District has 0.2 MG of total storage, and the distribution system consists of one pressure zone which is gravity fed by the two tanks. Low pressures are known to occur, especially in the School Road area, due to small diameter (2-in.) mains. Miranda’s water system is in fair to good condition. The primary deficiencies associated with the existing system are some undersized water mains and inadequate storage capacity. The District has 0.2 MG of total storage in the form of two 100,000 gallon tanks, one redwood and one bolted steel. The redwood tank was installed in 1964, and the bolted steel tank was installed in 1978. Both tanks are in good condition. The distribution system consists of one pressure zone, which is gravity fed by the two tanks. Low pressures are known to occur, especially in the School Road area, due to small diameter (2”) mains. This problem is exacerbated when fire hydrants are in use. The District has 20 fire hydrants. | Fair condition/ Upgrades planned/ identified | The system has had some action level exceedances for copper and lead in the past, but these issues seem to have been resolved by the addition of soda ash feed. | [6 empty] | septic - centralized collection | The Miranda CSD collection system consists of small diameter gravity sewer lines that collect effluent from individual septic tanks in the community. The system is a combined septic tank effluent gravity and pump system (STEG/STEP). The treatment plant has a dry weather design capacity of 46,000 gpd, as set forth in their waste discharge requirements. The Miranda CSD uses percolation ponds for disposal. This form of disposal is becoming increasingly difficult to permit due to stringent regulations governing disposal to the South Fork Eel River during the discharge prohibition period from May 15th through September 30th. This discharge prohibition period extends to all wastewater dischargers on Eel River as covered by the Water Quality Control Plan for the North Coast Region. | Regulatory - septic
y |  | MOBILE HOME ESTATES | 46037 | 1 |  |  | Other | 5761 Old Redwood Highway North SANTA ROSA, CA 95403 | n - contract with Willow CWD | y | y | 148 | water is included with rent | Unfamiliar; disinterested |  | 1 | 1 | 2 | 2 | 2 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 2 | 2 | 0 | 1 | 2 | 1 | 2 | 1 | 5761 Old Redwood Highway | Sonoma | North Coast, Region 1 | n | 320 | GW | well |  |  | 0-50 | $0 - $50 | No treatment but manganese levels are high and problematic in system | No treatment but manganese levels are high and problematic in system | Fair condition/ Upgrades planned/ identified |  | F | 1. Failure to submit 2014 Annual report to the Division 2. Total coliform monitoring and reporting violation for June 2015 3. Failure to comply with treatment technique 4. Treatment technique violation for July 2015 5. Citation for the source flow meter 6. Monitoring and reporting violation for November 2012 | 1. 7/17/15 2. 7/24/15 3. 7/29/15 4. 8/25/15 5. 7/25/17 6. 1/8/13 |  |  |  | sewer
|  | MONTAGUE, CITY OF | 40938 | 1 |  |  | City | P.O. BOX 428 MONTAGUE, CA 96064 |  |  |  | 503 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Siskiyou | North Coast, Region 1 | n | 1495 | SW | Lake Shastina - raw, Little Shasta River - raw | [8 empty] | C | 1. Violation of MCL for total Trihalomehtanes (TTHM) in drinking water | 1. 3/19/13
| y | MONTAGUE WATER CONSERVATION DISTRICT | 40938 | 1 |  |  | Water Conservation Dist |  | n | y |  | 50-100 | Uniform Rate Schedule | Familiar; infrequent participation | Funded | [18 empty] | 1 | 1 | Montague, Siskiyou County | Siskiyou | North Coast, Region 1 | n | 1,000-5,000 |  |  |  |  | $49 per acre/foot; Over $100 | $101 - $150
|  | MOONSTONE HEIGHTS MWA | 50417 | 1 |  |  | Mutual | P.O. Box 854 TRINIDAD, CA 95570 |  |  |  | 14 | [24 empty] | Humboldt | North Coast, Region 1 | n | 31 | GW | well | [8 empty] | 0 | 1. Failure to conduct or report monthly coliform sampling | 1. 8/14/14
|  | MOUNT WESKE ESTATES MUTUAL WATER COMPANY | 39614 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | MOUNTAIN VIEW MOBILE ESTATES, LLC | 44604 | 1 |  |  | Other | 2860 Santa Rosa Ave Santa Rosa, CA 95407 |  |  |  | 111 | [24 empty] | Sonoma | North Coast, Region 1 | n | 250 | GW | Wells (2)
y | y | MYERS FLAT M.W.S. INC. | 33438 |  | 1 |  | Mutual | P.O. BOX 74 MYERS FLAT, CA 95554 | y | n | y | 102 | Increasing block (graduated) rate schedule | Familiar; infrequent participation |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 0 | 2 | Myers Flat, CA | Humboldt | North Coast, Region 1 | n | 400 | GW | Wells (2) |  |  | 51-100; There is a base rate of $57.00 and a $8.00 surcharge which equals $65.00 total, excluding excess use charges. We also have an $8 surcharge for the CIP. | $51 - $100 |  | In the last 5 years we have started replacing the old lines with new and by 2020 hope to have all new lines and meters in place. | Fair condition/ Upgrades planned/ identified |  | 0 | 1. Failure to conduct or report monthly coliform sampling | 1. 10/14/14 | [7 empty] | 1
|  | NEWELL COUNTY WATER DISTRICT | 33909 |  | 1 |  | Water Dist | 405 5TH ST. TULELAKE, CA 96134 |  |  |  | 210 |  | Familiar; infrequent participation | Funded | [21 empty] | Modoc | North Coast, Region 1 | n | 300 | GW | Wells (3)
|  | NOEL HEIGHTS-CAL WATER SERVICE (PUC) | 40469 | 1 |  |  | Public Utility | 1720 NORTH FIRST STREET SAN JOSE, CA 95112 |  |  |  | 49 | [24 empty] | Sonoma | North Coast, Region 1 | n | 137 | GU | Well
y |  | NORTH GUALALA WATER COMPANY | 40185 | 1 |  |  | Public Utility | 38958 Cypress Way P.O. Box 1000 GUALALA, CA 95445 | y | y | y | 1052 | CPUC authorized rate structure based on expected expenses and revenues. Useage based with two tiers and fixed charges in combination. | Familiar; lack resources to participate |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 0 | 1 | 1 | 0 | 3 | 2 | Gualala, CA, Anchor Bay, and surrounding areas | Mendocino | North Coast, Region 1 | n | 2630 | SW | Instream - Big Gulch, Instream - Robinson Gulch, Wells (2 + 3 pending) |  |  | 51-100 | $51 - $100 |  |  |  | Occasional issues with non maintained leach fields in sources watersheds
|  | NORTH STAR MOBILE HOME PARK | 46037 | 1 |  |  | Other | 3200 Santa Rosa Avenue SANTA ROSA, CA 95407 |  |  |  | 76 | [24 empty] | Sonoma | North Coast, Region 1 | n | 75 | GW | Well | [8 empty] | 0 | 1. Nitrate monitoring and reporting violation for first quarter 2013 | 1. 6/10/13
|  | NOYO HARBOR DISTRICT | 31027 |  | 1 |  | Harbor Dist | [29 empty] | Mendocino | North Coast, Region 1 | n | [14 empty] | D | 1.Notice of Violation of 9/9/15 Water Quality Certification and Regional Water Board Order No. 86-51 | 1. 4/15/2016 2. 12/7/16
|  | OAK VALLEY ACRES P.O.A. | 25493 |  | 1 |  | Other | P O BOX 86 YREKA, CA 96097 |  |  |  | 26 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 80 | GW | Well
y |  | Odd Fellows Recreation Club | 40469 | 1 |  |  | other | 9090 Gilroy Avenue, Guerneville, CA 95446 | y | y | y | 259 |  | Unfamiliar; lack resources to investigate/participate |  | 0 |  | 1 | 1 | N/A | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | The Odd Fellows Recreation Club in Guerneville | Sonoma | North Coast, Region 1 | n | 80 | GW | Wells (3) | [14 empty] | sewer
| y | ORICK C.S.D. | 47621 | 1 |  |  | CSD | P.O. BOX 224 ORICK, CA 95555 | n | y |  | 140 | Increasing Block (Graduated) Rate Schedule | Familiar; infrequent participation | Funded | [5 empty] | 1 |  |  |  | 1 | 1 |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | Orick, CA | Humboldt | North Coast, Region 1 | n | 450 | GW | Wells (2) |  |  | 0-50 | $0 - $50 |  | The initial system construction of the water system served most of the residents of the Orick Community. The original system (1977-1978) consisted of two 60 foot wells with 10 hp submersible pumps, a 100,000 gallon redwood storage tank, and 8-inch, 6-inch, and 4-inch distribution lines. In 1978, an 8-inch line was extended southwest along the north side of Route. 101 in anticipation of the 1987 expansion. The 8-inch line was extended west past Hilton Road to the National Park Service Visitors’ Center in 1987. The pumping capacity of the District’s water system is approximately 288,000 gallons per day. The system demand is approximately 216,000 gallons per day. The system demand is approximately 75% of the system pumping capacity. Currently 139 of 142 service connections provided by the water facility are being served. The District maintains two active wells with a total production capacity of 0.274 MGD. The District maintains one pressure zone in its distribution system, serviced by approximately 6 miles of 4-inch through 8-inch PVC and AC pipe. The District’s storage capacity includes two 100,000 gallon redwood storage tanks. This represents less than one day of needed storage. Water service within Orick is generally good. A significant deficiency of the current water system is its lack of proper storage, which is less than one day at maximum day demands. | Storage capacity insufficient | [7 empty] | septic - centralized collection | Pollution from failing septic tanks has been found to be widespread and contaminating local groundwater sources. The Orick CSD applied to the Humboldt LAFCo to activate their latent powers to provide community wastewater services, with wastewater service to be limited to the commercial/residential areas of the Orick community along Hwy 101 on the north and south sides of Redwood Creek. LAFCo took action to authorize this additional power in May 2011. The Orick CSD recently evaluated alternatives for a community wastewater system and completed an EIR (State Clearing House No. 2009082034) evaluating a Septic Tank Effluent Pump system where effluent would be pumped through collection piping to an advanced treatment system and then disinfected and discharged to subsurface disposal field(s). The system was intended to have a design buildout to serve 371 equivalent residential units, and flows are expected to range between an average dry weather flow of 43,041 gpd to a peak day average flow of 86,081 gpd (Draft Environmental Impact Report Orick Wastewater Project Orick CSD, October 2011). Following this effort, the Orick CSD received funding from the North Coast Resource Partnership to conduct a demonstration project to evaluate the feasibility of a decentralized community wastewater system. The Orick CSD will need ultimately to identify a preferred wastewater system, design and feasible project, and seek regulatory approval and adequate funding. In the meantime, owners wishing to develop their land may do so using onsite sewage disposal systems. Site conditions may require that non-standard systems be used, such as Wisconsin Mounds or At-Grade systems that do not use subsurface leach lines for effluent disposal, which may require inspection and monitoring. | Fair condition/ Upgrades planned/ identified
y | y | ORLEANS C.S.D. | 40129 | 1 |  |  | CSD | P.O. Box 303 ORLEANS, CA 95556 | y | y | n | 139 | Increasing block (graduated) rate schedule | Unfamiliar; interested |  | 0 | 1 | 3 | 0 | 3 | 3 | 0 | 1 | 0 | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | Orleans, CA | Humboldt | North Coast, Region 1 | n | 630 | SW | IN- Pearch Creek - raw |  |  | 0-50 | $0 - $50 | Water flows by gravity to treatment, where it is prechlorinated and then filtered through three parallel Permutit automatic backwash filters. | Orleans CSD water supply consists of an infiltration gallery within Pearch Creek with unknown but adequate capacity. Orleans CSD currently uses inline filtration, which is no longer an accepted filtration technology in the State of California. As a result, the District has recently applied to fund a project which includes a fourth filter, turbidity meters, a second 100,000 gallon storage tank, and a new exit flow meter to replace the high flow turbine meter. Additionally, it has been proposed by the District to move the polymer and chlorine injection point further uphill from the current treatment point, which could provide the necessary flocculation time to change the system from inline to direct filtration (NCRP Demonstration Project for Orleans Community Services District, January 2015). The Orleans CSD received funding from the North Coast Resource Partnership to conduct a demonstration project to evaluate water demand, water storage, water rights, a water shortage plan, and develop strategies for addressing those needs. OCSD’s water supply consists of an infiltration gallery within Pearch Creek with unknown but adequate capacity. Water flows by gravity to treatment, where it is prechlorinated and then filtered through three parallel Permutit automatic backwash filters. The District recently began feeding polymer or other coagulant. Water is then stored in a 100,000 gallon redwood tank and fed to distribution. Two pressure zones exist within the system, with one zone served by the redwood storage tank and a second zone served by a booster pump. The distribution system consists of mostly asbestos cement pipe with some ductile iron, PVC, and steel, all ranging in size between 2 inches and 8 inches in diameter. The distribution system was installed in 1977 and 1997. | Fair condition/ Upgrades planned/ identified
|  | ORLEANS MUTUAL WATER CO. | 40129 | 1 |  |  | Mutual | P O BOX 54 ORLEANS, CA 95556 |  |  |  | 38 | [24 empty] | Humboldt | North Coast, Region 1 | n | 85 | SW | IN - Crawford Creek -raw |  |  |  |  | Orleans CSD currently uses inline filtration, which is no longer an accepted filtration technology in the State of California. As a result, the District has recently applied to fund a project which includes a fourth filter, turbidity meters, a second 100,000 gallon storage tank, and a new exit flow meter to replace the high flow turbine meter. Additionally, it has been proposed by the District to move the polymer and chlorine injection point further uphill from the current treatment point, which could provide the necessary flocculation time to change the system from inline to direct filtration (NCRP Demonstration Project for Orleans Community Services District, January 2015). The Orleans CSD received funding from the North Coast Resource Partnership to conduct a demonstration project to evaluate water demand, water storage, water rights, a water shortage plan, and develop strategies for addressing those needs. Orleans CSD water supply consists of an infiltration gallery within Pearch Creek with unknown but adequate capacity. |  |  |  | B | 1. Failure to comply with combined filter effluent turbidity performance standards 2. Failure to comply with combined filter effluent turbidity performance standards | 1. 6/15/2016 2. 10/21/14
|  | PACIFIC REEFS WATER DISTRICT | 39667 | 1 |  |  | Water Dist | P.O. Box 314, Albion, CA 95410 | n |  |  | 17 of 24 lots | tiered to encourage water conservation | Familiar; infrequent participation | Funded | [20 empty] | Pacific Reefs, a small 25-lot sudivision | Mendocino | North Coast, Region 1 | n | 48 | [6 empty] | All water flows through a chlorinator before being pumped into the District’s two storage tanks. | The District’s water supply consists of two springs and a well, both of which are located within the subdivision and District boundaries, and on District-owned land. The well is equipped with a pump that operates at approximately 1.5 gallons per minute (gpm). The spring water is also collected and pumped to the storage tanks. All water flows through a chlorinator before being pumped into the District’s two storage tanks. The storage tanks include a 40,000 gallon steel tank (which collapsed in May 2013) and a 20,000 gallon wooden tank. The District is planning to replace the 40,000 gallon tank. The existing storage is estimated to be the equivalent of 57 days of average usage. A number of lot owners have private wells; however, the District has infrastructure in place and provides backup water service in the event of well failure. The District owns the small parcel on which the spring/well and water storage tanks are located, as well as the two water tanks and pumphouse facilities. The storage tanks include a 40,000 gallon steel water tank (now collapsed and to be replaced), a 20,000 gallon wooden tank, both built in 1960 and renovated in 2005. The useful life of the water system is estimated at 15-30 years. | Good condition
|  | PALMER CREEK CSD | 49403 | 1 |  |  | CSD | P.O. Box 309 FORTUNA, CA 95540 |  |  |  | 131 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Humboldt | North Coast, Region 1 | n | 320 | GW | Well |  |  |  |  | Water pumped from the wells is injected with chlorine and then sent to a contact basin prior to filtration through a Loprest package treatment plant designed to remove iron and manganese from the groundwater. The plant consists of a reaction vessel and three pressure filters, after which water is boosted to storage and distribution. | Palmer Creek CSD’s water supply consists of two active wells, each capable of pumping 80 gpm. The District has one 200,000 gallon storage tank that serves two pressure zones; one has reduced pressures through a PRV. The distribution system consists of approximately 38 miles of PVC, cast-iron and asbestos cement pipe ranging in size from 2 inches to 10 inches. Palmer Creek CSD produced more than 11 million gallons of drinking water in 2003. Average daily use is estimated at approximately 0.031 MGD, and peak daily use is estimated at approximately 0.084 MGD. The District has approximately 150 service connections, of which 127 are active connections. All active connections are metered. The Palmer Creek CSD water distribution system was constructed in 1997. Palmer Creek CSD produced more than 11 million gallons of drinking water in 2003. Average daily use is estimated at approximately 0.031 MGD, and peak daily use is reported at approximately 0.084 MGD. The District has approximately 128 metered water service connections. The water system was designed to serve 187 residential connections. Based on present and projected water use levels, Palmer Creek CSD has the ability to meet the water demands of development of the remaining lots in the District without the need to supplement supplies or storage and delivery systems. (Humboldt LAFCo - Palmer Creek CSD Municipal Service Review, 2007) | Good condition | [7 empty] | sewer | The Palmer Creek CSD collects wastewater from service connections within its District and conveys it to a metered interconnection point with the City of Fortuna wastewater system for treatment and disposal, pursuant to a contract for service. There are 154 existing residential wastewater connections within the Palmer Creek CSD generating an average dry weather flow of 20,000 gpd (gallons per day) and wet weather flows of 30,000 gpd (Humboldt LAFCo - Palmer Creek CSD Municipal Service Review, 2007). The Palmer Creek CSD reports that it is currently at its contracted limit for wastewater flows. The contract with the City would need to be amended to allow additional development within the District. Discussions regarding the wastewater agreement between the City and the District are ongoing. | Adequate
y |  | PALOMINO ESTATES M.W.C. | 36371 |  | 1 |  | Mutual | 111 PALOMINO WAY GARBERVILLE, CA 95542 | y | y | n | 19 | Monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 2 | 0 | Palomino Estates on East Branch Rd. in Benbow Ca., Garberville is all Benbow residents mailing address. | Humboldt | North Coast, Region 1 | n | 64 | SW | IN - Eel River infiltration gallery - raw |  |  | 100-150 | $101 - $150 | triple media filter for arsenic |  |  |  | A | MCL Total coliform violation June 2017, Total coliform monitoring violation for April 2017, monitoring and reporting violation for June 2017 | 7/25, 2017 |  |  |  | septic | each home has own septic | Adequate |  | 1
|  | PALOMINO LAKES MUTUAL WATER CO. | 37411 |  | 1 |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | PARK ROYAL MUTUAL WATER | 46037 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | PATRICK CREEK COMMUNITY SERVICE DISTRICT | 46708 | 1 |  |  | CSD | 5045 Patrick Creek Drive Mckinleyville, CA 95519, 707.839.2355 | [28 empty] | Humboldt | North Coast, Region 1 | n | 70 | [7 empty] | The District originally had its own water system. However, in 1973, the Patrick Creek Community Services District (PCCSD) transferred interest in the distribution system to the McKinleyville Community Services District where water obtained from the HBMWD is distributed. The water system currently serves 17 homes, with a total capacity of 18 homes. One household has two lots, and the rest are single lots. With the exception of the possibility of the double lot ownership, the district is at capacity. | Adequate
| y | PHILLIPSVILLE C.S.D. | 33438 |  | 1 |  | CSD | P.O. BOX 231 PHILLIPSVILLE, CA 95559 | n | y |  | 66 | Increasing Block (Graduated) Rate Schedule | Unfamiliar; interested | [8 empty] | 1 | [12 empty] | Phillipsville, CA | Humboldt | North Coast, Region 1 | n | 300 | SW | Spring - raw, Well |  |  | $0-50 | $0 - $50 | The well is continuously disinfected with a chlorination feed system located in the well housing. | PCSD’s water supply consists of a groundwater well of unknown capacity and a surface water spring source with variable capacity. The spring source is unable to meet summertime demands, and therefore only serves the upper portion of the system during low flows while the well supplies water to the rest of the system. The well is primarily used during dry months. The spring is believed to be under the influence of surface water, is not filtered, and is continuously chlorinated. The system has a total of eight storage tanks ranging in size from 250 gallons to 60,000 gallons for a total combined capacity of 74,850 gallons. The system has numerous small pressure zones with anywhere between two and four connections. The distribution system consists of a variety of piping, not all of which meet standards. The exact amounts of any particular piping are unknown. Some electrical conduit is currently being used for water piping. The system has replaced approximately 2,050 feet of piping since 2000 with PVC piping. According to the 2004 DHS annual inspection report, PCSD retailed an estimated 8.75 million gallons of drinking water in 2003. Average daily use for the entire District is estimated at 0.024 mgd, and peak daily use is estimated at approximately 0.085 mgd. The Phillipsville area has approximately 65 active service connections. The system does not have a master meter to monitor production. The Phillipsville CSD water system was in poor condition with inadequate storage capacity, a distribution system consisting of non-standard materials such as electrical conduit, limited source capacity, and lack of treatment. The District received American Recovery and Restoration Act funding through DDW and upgraded the water system infrastructure to resolve these issues. The project included the installation of a treatment plant on the spring source, the replacement of distribution pipes, and the installation of a 140,000 gallon storage tank. The project was completed in 2012. The improvements were designed to serve existing development plus ten percent additional capacity to accommodate some growth. The state DDW reports issues with the system remain relating to the turbidity of water that feeds a spring that serves the upper portion of the District and the need for additional storage. The drinking water system is adequate for current needs and does not have significant deficiencies (2014 Housing Element Attachment J, Detail of Infrastructure and Service Needs of Legacy Communities). | Fair condition/ Upgrades planned/ identified | The well has high levels of iron and manganese and suffers from low pH, which causes problems with coloration and corrosion of the distribution system.
|  | Pine Cove RV Park | 39583 | 1 |  |  |  | 9435 TRINITY DAM BLVD. #5 LEWISTON,CA 96052 |  |  |  | 68 | [24 empty] | Trinity | North Coast, Region 1 | n | 255 | GW | Wells (2)
y |  | PINE GROVE Mobile Home PARK | 26544 |  | 1 |  | other | 2100 NORTHCREST DRIVE CRESCENT CITY, CA 95531 | n - contract with Willow CWD | y | y | 51 | included with rent | Unfamiliar; disinterested |  | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 |  | 1 | 1950 Northcrest Dr. & 2200 Northcrest Dr. Crescent City Ca. | Del Norte | North Coast, Region 1 | n | 100 | GW | well | [7 empty] | Chromium6 exceedence. | [6 empty] | sewer
y |  | PINE MOUNTAIN MUTUAL WATER CO. | 32667 |  | 1 |  | Mutual | 4551 Ridgewood Road WILLLITS, CA 95490 | y | y | n | 124 | Monthly/ annual flat rate | Unfamiliar; interested |  | 1 | 3 | 1 | 0 | 2 | 2 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 3 | 0 | 0 | 2 | 1 | 3 | 2 | Pine Mountain Estates, Willits, CA | Mendocino | North Coast, Region 1 | n | 310 | SW | IN - Chinquapin Lake intake - raw |  |  | 61 - 80 | $51 - $100 |  | The Company owns and maintains three active wells, the Chinquapin Lake Intake, approximately six miles of pipeline, and a pump station. | Adequate | The Safe Drinking Water Information System lists the more recent monitoring violation dated 2013 with compliance achieved June 3, 2013. The USEPA notesone monitoring and reporting violation on record dated March 31, 2013,with compliance achieved July 6, 2016 for this water system. | C | 1. Failure to sample for disinfection byproducts 2. Compliance order for violation of section 116555 of the California Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 6/3/13 2. 10/17/14 | [7 empty] | 1
|  | PLAZA MOBILE HOME PARK | 29250 |  | 1 |  | other | 871 38TH AVENUE SANTA CRUZ, CA 95062 |  |  |  | 71 | [24 empty] | Sonoma | North Coast, Region 1 | n | 125 | GW | Well (2)
|  | POINT ARENA WATER WORKS | 40208 | 1 |  |  | private water company | P.O. BOX 205 POINT ARENA, CA 95468 135 Hay Parkway, Pt Arena, CA 95468 |  |  |  | 194 | [23 empty] | City of Point Arena | Mendocino | North Coast, Region 1 | n | 646 | GW | Well (2) | [5 empty] | The Garcia River is the primary water supply for the company, which withdraws water from one 24-inch diameter well and one 12-inch well. Three secondary wells at Whiskey Shoals are also utilized. An average of 12,370 CCF (hundreds of cubic feet) are pumped each year, which is equivalent to 9.2 million gallons or 28.4 acre feet per year. Average water usage is 87 gallons per residential customer per day, which is very low and indicates water conservation measures are in place. Company storage facilities include a 285,000 gallon concrete tank and a 272,000 wooden tank. The water distribution system is via approximately 46,000 lineal feet of pipe, primarily 6-inch, 8-inch and 12-inch, although some 2-inch and 4-inch lines are still in use. Although the company’s infrastructure is in relatively good shape, water storage and insufficient fire-flow problems were identified in a 2004 report, the “Water System Master Plan and Feasibility Analysis.” Water storage for firefighting is addressed above. Limitations on fire flow water occur in Zone 1 (the downtown area), which has existing 6-inch water lines. These lines will not be replaced until there are sufficient funds to do so. (William Hay, PAWW; personal communication). PAWW has a current application pending before the CPUC to renew its permit for up to 100 acre-feet of water per year; and a second application to add another 50 acre-feet to the allocation. | Storage capacity insufficient
|  | Point Arena WWTP | 40208 | 1 |  |  | Sanitary Dist | Iverson Road, Point Arena, CA 95468 |  |  |  | 364 | [24 empty] | Mendocino | North Coast, Region 1 | n | 450 | [17 empty] | The City operates and maintains a Wastewater Reclamation Facility (treatment plant); approximately 11,000 lineal feet of 6-inch diameter sewage collection mains; one pump (lift) station; and four 17,000 square foot percolation ponds. The treatment plant is located at the intersection of Iverson Avenue and Port Road adjacent to Arena Creek. The lift station is located at the Arena Cove parking area. The percolation ponds are located on top of the south bluff off Bluff Top Road.The treatment facility is designed to provide secondary treatment for up to 0.13 million gallons of wastewater per day (mgd), average dry weather flow. Treatment consists of two aerated ponds which operate in series, followed by disinfection prior to being discharged to the percolation ponds. Pumps are utilized to transport the chlorinated effluent via an 8-inch force main 3,400 feet to the ponds. The ponds have sufficient capacity during most of the year. However, during large wet weather conditions, the ponds are not able to keep up with the effluent flows so a 20 -acre pasture is utilized for treated effluent spray irrigation. The pasture is located on the bluff adjacent to the percolation ponds.The wastewater system operates under waste discharge requirements of the North Coast Region, California Regional Water Quality Control Board including Monitoring and Reporting Program No. R1-2003-001. The treatment plant currently treats an average of 0.0383 mgd, dry weather flow; and 0.0797 mgd, wet weather flow. Improvement recommendations were made in a 2006 sewer system analysis by Coastland Engineering, and include replacing specific line segments, repairing laterals and manholes to reduce inflow and infiltration (I&I), and improvements to the treatment ponds. A more recent engineering study by Winzler & Kelley in 2010 addressed sludge removal and I&I. | Fair condition/ Upgrades planned/ identified
|  | RAINS CREEK WATER DISTRICT | 49732 | 1 |  |  | Water Dist | P.O. BOX 956 FORESTVILLE, CA 95436 |  |  |  | 64 | [24 empty] | Sonoma | North Coast, Region 1 | n | 180 | GW | Well | [8 empty] | C | 1. Compliance order for violation of section 116555 of CA Health and Safety Code, which requires each public water system to have a reliable water supply for its customers. | 1. 10/17/2014
|  | RANDAL'S RANCHETTE MUTUAL WATER CO. | 46037 | 1 |  |  | Public Utility | [29 empty] | Sonoma | North Coast, Region 1 | n
| y | REDCREST WATER WORKS | 48542 | 1 |  |  | other | P.O. BOX 282 REDCREST, CA 95569 | n | y |  | 35 | Monthly/ Annual Flat Rate | Unfamiliar; interested | [19 empty] | 1 | 1 | Redcrest, CA | Humboldt | North Coast, Region 1 | n | 100 | SW | IN - Chadd Creek - raw |  |  | $0-50 | $0 - $50
| y | REDWAY C.S.D. | 37778 |  | 1 |  | CSD | P.O. BOX 40 REDWAY, CA 95560 | y | y |  | 687 | Monthly/ Annual Flat Rate | Familiar; not a participant | [20 empty] | 1 | Redway, CA | Humboldt | North Coast, Region 1 | n | 1500 | SW | IN - Eel River Infiltration Gallery - raw |  |  | $50-100; Res. $60.00 goes by use; Commercial $64. per month and goes up by use. | $51 - $100 |  | The District’s water system consists of two water sources, a conventional filter water treatment plant, three storage facilities, two pressure reduction vaults, and one booster pump station, as well as the transmission and distribution lines, many of which were installed prior to 1950. There are presently 600 service connections. The sources of water are the South Fork of the Eel River (surface water) and an unnamed spring (ground water). The water treatment plant design capacity is 460,000 gallons per day. The water permit allows for a draw of 1.05 CFS. The spring source is limited to .123 CFS, and 52 AC-FT per year. The maximum production for the spring is 46,000 gallons per day. The total capacity of the three storage areas is approximately 380,000 gallons. Additional storage capacity is indicated for fire safety during high use periods, which coincide with the highest fire danger seasons. There are areas within the district that are in the planning stages of subdivision; the developer would have to provide the needed additional storage capacity to enable the District to provide services to numerous additional customers Redway CSD’s water system consists of two water sources, an infiltration gallery in the South Fork of the Eel River and an unnamed spring, which is “inactive”. The Redway CSD’s total storage capacity is approximately 735,000 gallons in the residential area and 100,000 gallons in the Meadows Industrial Park. The District maintains approximately 25 miles of distribution piping, which is reported to have inadequate pressure in portions of the system during fire flows. The Redway CSD completed a project to address water system deficiencies in 2009. The District received funding through DDW and upgraded piping and valving to improve the operation and performance of the water treatment system and rehabilitated the Eel River intake. According to WaterWorks Engineers (WWE), Redway CSD Water and Wastewater Systems Capacity Analysis, 2014, “(t)he water treatment plant is limited by the design flows of the water intake pumps and booster pumps, and the pretreatment system to a capacity of 450 gpm. At the current Maximum Day Demand of 494,000 gallons, the water plant has to run 18.3 hours per day at its full output of 450 gpm in order to provide this volume of water. This should be viewed as essentially at capacity, because the plant is not staffed 24 hours per day, and while the bulk of the treatment process is automated, it is not designed for complete un-manned operation. Depending on the demand of significant new connections to the water system, the (Water Treatment Plant) capacity would need to be increased.” “It is the opinion of WWE that water treatment system is currently at capacity, and the water storage and distribution system is already struggling to meet the demands of existing connections. These issues should be addressed before substantial additional service connections are made.” | Fair condition/ Upgrades planned/ identified | [8 empty] | According to the Redway CSD Water and Wastewater Systems Capacity Analysis, WWE 2014, “(t)he most limiting facility at the treatment plant currently is the sludge dewatering process. Dewatering capacity is currently sufficient during the dry weather season, but not during the wet-weather season.” “The next item of concern is the peak hour wet weather flow hydraulic capacity of the piping downstream of the secondary clarifier overflow weir. Instantaneous flow above approximately 665 gpm will submerge the weir. This can be alleviated by upsizing the piping downstream of the clarifier from 8-inch to 10-inch, but this is not critical for short-term operation. “ “The last item of concern is the existing oxidation ditches apparent inability to denitrify at a level that will be necessary to achieve an anticipated future 10 mg/L nitrate limit. The existing WWTP may be able to meet this limit by closely monitoring immersion of the existing brush aerator and other process parameters, but it appears to be already close to its treatment capacity even if denitrification performance is optimized.” “Several options exists for improving the denitrification capacity of the plant, including 1) supplementing the existing oxidation ditch with a pre-anoxic basin and internal mixed liquor recycle pumping provisions, 2) installation of a new oxidation ditch in parallel to the existing oxidation ditch, or 3) installation of a new, stand-alone oxidation ditch and re-tasking of the existing oxidation ditch to an ancillary facility such as emergency overflow, aerobic digester, etc. However, all of the options would be costly, and would require procurement of funding assistance in order to implement.” In particular, the Redway CSD Water and Wastewater Systems Capacity Analysis concludes that “The existing wastewater treatment plant may not be capable of complying with what is believed to be a forthcoming effluent discharge limit for nitrate of 10 mg/L, at current wastewater flows and loads. It is very unlikely that it would be able to meet the 10 mg/L limit with increased flows and loads.” | Fair condition/ Upgrades planned/ identified
y |  | REDWOOD HEIGHTS WATER ASSOCIATION | 49886 | 1 |  |  | Mutual | 190 S. ORCHARD AVE., STE B220, VACAVILLE, CA 95688 | n | n | y | 17 | monthly/ annual flat rate | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 2 | Redwood Heights Dist. in Cazadero, CA | Sonoma | North Coast, Region 1 | n | 30 | GW | Well | [8 empty] | 0 | 1. Total coliform monitoring and reporting violation for 3/14 2. Total coliform monitoring and reporting violation for May 2017 | 1. Total coliform monitoring and reporting violation for 3/14 2. Total coliform monitoring and reporting violation for May 2017 | D | 1. NOV: failing to divert surface runoff to prevent drainage from sludge treatment and storage sites | 1. 3/10/17 | septic | individual systems (17) | Adequate
y |  | REDWOOD PARK C.S.D. | 27200 |  | 1 |  | CSD | P.O. BOX 650 KLAMATH, CA 95548 | n | n | y | 44 | uniform rate schedule | Unfamiliar; disinterested |  | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Redwood Park, CA | Del Norte | North Coast, Region 1 | n | 200 | GW | Well (3) |  |  | 0-50 | $0 - $50 |  | The RPCSD water system facilities include: one 60 foot deep groundwater well, a gravity fed pipeline distribution system, one 15 horsepower pump and two redwood storage tanks including one 60,000 gallon and one 150,000 gallon tank. The RPCSD water is metered, and is typically supplied to homes through ¾-inch supply lines. The District’s 150,000 gallon redwood water tank is leaking and needs replacement. Some of the system’s piping currently needs repair/replacement and the District needs additional storage capacity to adequately provide water in an emergency. | Fair condition/ Upgrades planned/ identified | [8 empty] | The RPCSD’s wastewater system consists of 0.25 miles of six inch mains, a gravity collection system, two lift stations, Imhoff tank, and five-acre leach field. The wastewater treatment facility is located adjacent to and east of the District Boundary and has a capacity of 15,400 gallons per day (RPCSD, 2009). The wastewater system adequately serves District residents at this time. The sewer mains will need replacement in the future. | Adequate
y |  | Reservation Ranch | 42944 | 1 |  |  | other | 370 Sarina Road, Smith River | y | n | don't know | 21 | We do not have rates. This is a small, private system serving owner and employees. | Unfamiliar; disinterested |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 0 | 2 | 2 | Reservation Ranch, private system | Del Norte | North Coast, Region 1 | n | 50 | GW | well |  |  | n/a | [8 empty] | C | 1. Notice of Violation and CA WC Section 13267 Order for Technical Reports: unlawful discharges of waste into waters of the state (violations of Conditional Waiver of Waste Discharge Requirements for Existing Cow Dairies in the NC Region). 2. Notice of Violation of CWC Section 13267 Order for Technical Reports, Staff's recommendation. Failed to submit technical reports 4/6/17 3. NOV: CWC Section 13267 Order for Technical Reports | 1. 1/9/2017 | septic
y | y | RESORT IMPRVMT. DIST. #1 | 41140 | 1 |  |  | Resort Imp Dist |  | y | y | y | 470 | montly/ annual flat rate; increasing block (graduated) schedule; wastewater is a monthly flat rate for residential and commercial users, and water is billed under a tiered use structure, so monthly bills vary tremendously based upon water use. | Familiar; lack resources to participate | Funded | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | Shelter Cove, CA | Humboldt | North Coast, Region 1 | n | 324 |  |  |  |  | 100-150 | $101 - $150 |  | The RID water source consists of two active surface water spring intakes (Rick Spring and Upper Telegraph Creek), a seasonal standby surface water spring intake (Lower Telegraph Creek), and two standby wells. During summer months when demands are high, the District is required to maintain environmental flows within Telegraph Creek and is allowed to withdraw at Lower Telegraph Creek at a point prior to the water’s infiltration into beach sands. The source capacity of the District is approximately 508 gpm (0.732 MGD), well over current maximum day demands (230 gpm). The treatment capacity of the plant is 350 gpm, or 0.504 MGD. Water service within the RID is generally very good.The district maintains 12 storage tanks (welded steel and redwood) ranging in size from 0.03 MG to 1 MG. The distribution system consists of approximately 44 miles of water main of varying size. The majority of the distribution system is asbestos cement (AC) pipe, but some above ground cross-country steel and polyvinyl chloride (PVC) is also present. The District is in the process of locating additional source capacity. The RID has identified sites for new water wells, several of which have been approved by the state for service. The RID Board has approved funds for the exploration of five new well sites to be located in regions of the upper Cove where successful well sites have been established and geologic conditions are similar (Resort Improvement District #1 General Manager’s Report, February 2012). The District’s water supply system consists of a diversion facility and treatment plant on Telegraph Creek. The distribution system has been extended throughout the District and contains 18 storage tanks and 10 booster pump stations. Although the distribution system was installed District-wide, the initial water appropriation rights were not sufficient to meet projected demand for full build-out. | Uncertain water supply | [7 empty] | sewer | The service includes wastewater collection, treatment, and disposal. RID’s collection system incorporates both gravity mains and nine lift stations. The wastewater treatment plant (WWTP) consists of coarse screening, two oxidation ditches, two clarifiers, and chlorination/de-chlorination facilities. Based on existing flows, the District is approximately at 59% of dry weather treatment capacity and approximately 78% wet weather capacity at its WWTP. The District is currently under an Administrative Civil Liability Order due to the District’s inability to meet treatment requirements. In essence, the influent to the treatment plant is so diluted, it is virtually impossible to meet these requirements. The District last developed a Master Plan Update for its wastewater treatment and disposal facilities in 1997, which outlines necessary improvements to meet different forecasted growth scenarios. The District also developed a ten-year capital improvement program in 2007 to address required maintenance and upgrades to their wastewater system. The District instituted an I&I rehabilitation program in February 2008 as a compliance project in response to Administrative Civil Liability Order No. R1-2007-0009. The District has continued to complete inspections and point repairs of the collection system, including improvements to manholes. According to the approved Waste Discharge Requirements/ Permit (R1-2015-0017), although the design peak daily wet weather flow was exceeded in 2012 (0.818 mgd), the facility remained below the design peak daily wet weather flow of 0.77 mgd for the most recent 4 years (0.568 mgd). | Adequate
|  | RIDGEWOOD WATER SYSTEM | 32667 |  | 1 |  | Mutual | 16200 N HWY 101 WILLITS,CA 95490 |  |  |  | 167 | [24 empty] | Mendocino | North Coast, Region 1 | n | 270 | GU | Springs (3), well | [8 empty] | 0 | 1. Nitrate and nitrite monitoring and reporting violations 2. Failure to comply with the Condition #17 of Domestic Water Supply Permit No. 02-03-02P23002 | 1. 9/17/14 2. 12/13/12
|  | RIEBLI MUTUAL WATER COMPANY | 42958 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | RINCON VALLEY MOBILE ESTATES | 44390 | 1 |  |  | Other | P.O. Box 7 NOVATO, CA 94948 |  |  |  | 230 | [24 empty] | Sonoma | North Coast, Region 1 | n | 460 | GW | Wells (2)
y | y | RIO DELL, CITY OF | 47639 | 1 |  |  | City | 675 WILDWOOD AVE. RIO DELL, CA 95562 | y | y | y | 1233 | There is a base charge and a volume charge, monthly. | Familiar; regular participant | Funded | 3 | 1 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 1 | 1 | 2 | 2 |  | Rio Dell, CA | Humboldt | North Coast, Region 1 | n | 3174 | SW | Eel River - raw |  |  | $61.83/month water and $71.39/month sewer | $101 - $150 | The City’s water supply comes from a recently completed infiltration gallery in the South Fork of the Eel River. The production capacity of the gallery is tied to water levels within the river, such that in the winter the pumps can deliver around 700 gpm, but in the summer production falls to about 550 gpm (0.792 MGD). Water is pumped to treatment for filtration and disinfection before entering the City’s distribution system. The Metropolitan Wells project provided a state-of-the-art filtration system upon the City's old well site and added an additional layer of water security for the City. Moving forward, the City is working on obatinaing State grants through Proposition 1 to rehabilitate aged water lines and replace water storage systems. | The City’s water supply comes from a recently completed infiltration gallery in the South Fork of the Eel River. The production capacity of the gallery is tied to water levels within the river, such that in the winter the pumps can deliver around 700 gpm, but in the summer production falls to about 550 gpm (0.792 MGD). Water is pumped to treatment for filtration and disinfection before entering the City’s distribution system. The City has two pressure zones served by four tanks ranging in size from 100,000 gallons to 500,000 gallons for a total combined storage capacity of 1.1 million gallons. The distribution system contains approximately 11 miles of pipe, of which 5 miles were replaced with 10” HDPE pipe under the City’s infrastructure rehabilitation project. The remaining distribution system ranges in size from 4 inches to 6 inches and consists mainly of AC pipe. The City has recently invested heavily in upgrading its water system following a declared water emergency in 2001 when the City’s water supply began to fail. Since then, they have received $5.0 million in grant funds to rehabilitate the water distribution system city-wide and $1.0 million in grant funds and a loan in the amount of $2.3 million to construct a new infiltration gallery and water treatment plant. The new treatment plant has a design capacity of 700 gpm. | Good condition |  |  | 1. Category 2 Pollutant (Effluent Violation for Group 2 Pollutant) | 1.15.2019 |  |  |  |  | The city has identified several wastewater facility improvement projects and continues to seek grant funding. The first is to address the collection system’s high inflow and infiltration (I/I). Surface stormwater and seasonally high groundwater is a significant contributor to I/I in Rio Dell. Poor drainage in areas of the city causes ponding and flooding leading to I/I. The city has been working to identify areas of the city where stormwater ponding and flooding has been historically problematic and is near wastewater pipes and therefore directly contributing to I/I. The city reports they are actively seeking grant funding to complete a comprehensive Sanitary Sewer Evaluation Study (SSES). | Fair condition/ Upgrades planned/ identified | The City is in the process of a drainage project for repairs and upgrades to severely degraded or inoperable portions of the stormwater system in various locations in the city, including culvert replacement and repair, completed in 2018. The City reports that future projects are planned, but still in need of financing.
y |  | (Russian) RIVER ESTATES MUTUAL WATER COMPANY | 19356 |  | 1 |  | Mutual | 151 LAWS AVENUE UKIAH, CA 95482 | n | y | y | 82 | uniform rate schedule | Familiar; not a participant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Russian River Estates, Ukiah Valley, CA 95482 | Mendocino | North Coast, Region 1 | n | 250 | GW | Wells (3) |  |  | 61-80 | $51 - $100 |  | The Company owns and maintains 2 active wells, 1 standby well, and approximately 9,000 feet of pipeline. In addition, the Company owns and operates two storage tanks. They participate in cooperation with Willow County Water District for shared facilities andadministrative and operations services. | Adequate
|  | Riverbend Mobile Home Park | 28277 |  | 1 |  | other | 45630 Highway 36 BRIDGEVILLE,CA 95526 |  |  |  | 28 | [24 empty] | Humboldt | North Coast, Region 1 | n | 60 | GW | Well | [8 empty] | 0 | 1. Failure to monitor for coliform bacteria in drinking water 2. Failure to monitor for coliform bacteria in drinking water | 1. 1/11/2017 2. 2/22/17
y | y | RIVERSIDE CSD | 52679 |  |  | 1 | CSD | 790 Centerville Rd FERNDALE, CA 95536 | y |  |  | 99 | monthly/ annual flat rate | [22 empty] | Ferndale rural areas from Port Kenyon to Centerville Road. | Humboldt | North Coast, Region 1 | n | 293 | GW | Wells (4) | [5 empty] | The District’s water source consists of three wells with a maximum production capacity of approximately 74,000 gallons of water a day. The District water source consists of artesian springs and wells with a maximum production capacity of approximately 60,000 gallons of water a day.Water service within the Riverside service area is generally good. Current peak water use is at approximately 62% of available production capacity. The District’s deep well can only be used as an auxiliary well due to high manganese content. The District does not currently have any fire hydrants and is not capable of supporting fire suppression. |  | The District’s deep well can only be used as an auxiliary well due to high manganese content.
|  | ROLLING OAKS ROAD ASSOCIATION | 49726 | 1 |  |  | Other | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | ROSELAND MOBILE HOME PARK | 46037 | 1 |  |  | other | 1355 Sebastopol Road SANTA ROSA, CA 95407 |  |  |  | 70 | [24 empty] | Sonoma | North Coast, Region 1 | n | 130 | GW | Wells (2)
y | y | RUSH CREEK MUTUAL WATER SYSTEM | 40455 | 1 |  |  | Mutual | P.O. BOX 18480 WEAVERVILLE, CA 96093 | y | y | y | 37 | Increasing block (graduated) rate schedule | Familiar; regular participant | Unfunded | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | Rush Creek Estates, Rush Creek Drive, Trinity County | Trinity | North Coast, Region 1 | n | 80 | SW | Rush Creek - raw |  |  | 51-100 | $51 - $100
y |  | RUSSIAN RIVER COUNTY SANITATION DISTRICT | 46037 | 1 |  |  | Sanitary Dist | (LOCATION: 18400 NEELEY RD., VACATION BEACH, CA (MAILING:) 404 AVIATION BLVD., SANTA ROSA, CA 95403 | y | y | y | 1,000 - 5,000 | monthly/ annual flat rate | Familiar; regular participant |  | 1 | n/a | n/a | n/a | 3 | 3 | 0 | 0 | 1 | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | The RRCSD includes the unincorporated areas of Rio Nido, Guerneville, Guernewood Park and Vacation Beach | Sonoma | North Coast, Region 1 | n | [5 empty] | Property tax charges, $1484 per ESD (1 unit) wastewater only; estimate 100-150 | $101 - $150 | [10 empty] | sewer | In the past, projects for wastewater treatment systems have not ranked high enough to receive IRWM funding, even though they are serving DACs. Wastewater treatment projects don't include a broad array of partners and the projects are not particularly compelling in a competitive environment. Concerns/challenges with sustainability/state continuing funding of IRWM programs; our wastewater projects do not have collaborations with other entities and are not attractive projects for the IRWM Program. The wastewater projects we submitted did not get funded. | Fair condition/ Upgrades planned/ identified |  |  | 1
| y | SALYER HEIGHTS W.S., INC | 35104 |  | 1 |  | Public Utility | P.O. BOX 156 SALYER, CA 95563 | n | n |  | 42 | Monthly/Annual Flat Rate | Familiar; infrequent participation | [20 empty] | 1 | Salyer Heights, CA | Trinity | North Coast, Region 1 | n | 82 | SW | Huckleberry and Shaber Creeks, IN - raw |  |  | $180 a year | $0 - $50 |  |  |  |  | B | 1. Failure to comply with combined filter effluent turbidity performance standards | 1. 2/17/17
|  | SALYER MUTUAL WC (FORMERLY RIVERVIEW AC) | 35104 |  | 1 |  | Mutual | P.O.Box 484 SALYER, CA 99563 |  |  |  | 64 |  | Familiar; infrequent participation | Funded | [21 empty] | Trinity | North Coast, Region 1 | n | 201 | SW | Trinity River infiltration well, IN - raw
| y | SANTA ROSA MOBILE ESTATES | 49306 | 1 |  |  | other | P.O. Box 176 Sebastopol, Ca 95473 | n | y |  | 141 | [23 empty] | Santa Rosa Mobile Estates Mobile Home Park located in Santa Rosa, Ca. / Sonoma County | Sonoma | North Coast, Region 1 | n | 420 | GW | Wells (3)
y |  | SAWYERS BAR COUNTY WATER DISTRICT | 32500 |  | 1 |  | Water Dist |  | n | y | n | 30 | monthly/ annual flat rate | Familiar; lack resources to participate |  | 1 | 3 | 3 | n/A | 3 | n/a | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | Sawyer's Bar, CA | Siskiyou | North Coast, Region 1 | n | 50 |  |  |  |  | Over $150 | > $150 | [14 empty] | 1
|  | Scotia CSD | 48542 | 1 |  |  | CSD | po Box 245, Scotia, CA 95565 |  |  |  | 308 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Humboldt | North Coast, Region 1 | n | 850 | SW | IN - Eel River, raw | [5 empty] | The Scotia CSD water supply comes from an infiltration gallery in the Eel River that supplies separate domestic water and raw water fire systems. In January 2016, the Scotia CSD adopted a resolution approving a letter of intent to accept all dedicated facilities and properties from the Town of Scotia, LLC, to provide utility and other services to the former mill town. The Scotia CSD has since adopted rates for water and sewer services and agreed to assume responsibility, accept the dedicated properties, and own and operate the systems thereafter. These rates include funding to carry out the necessary improvements to the water and wastewater systems, including a new water treatment plant above the 100-year flood elevation. | Fair condition/ Upgrades planned/ identified | The Scotia CSD WWTP is located within the 100-year floodplain. The treatment capacities of multiple unit processes within the facility are exceeded even by average day maximum month flows (Winzler & Kelly, 2006). However, under current conditions the three treatment ponds at the WWTP provide the necessary treatment to meet current permit conditions (SHN, 2007). In 2006, there was concern that the facility would not meet the secondary treatment standards for treatment. PALCO requested the facility be placed under a cease and desist order that set forth a time schedule for compliance with permit requirements relating to treatment. The cease and desist order was rescinded in April 2012 and a new permit was issued (ORDER NO. R1-2012-0065). The new permit states that “(a) hydraulic study was conducted during the term of the permit and determined that the design average dry weather flow of the WWTF is 1.0 MGD. Annual average flows at the Facility are approximately 0.200 MGD.” The Scotia WWTP currently discharges to percolation ponds adjacent to the Eel River during the summertime discharge prohibition period. The town will likely have to find alternative methods for summertime disposal, as percolation ponds on the Eel River are becoming more difficult to permit with time. As indicated above, the Scotia CSD has assumed responsibility for the wastewater system and is responsible for carrying out the LAFCo conditions of approval for the formation of the Scotia CSD, which specifies certain wastewater system improvements. | B | 1. Failure to comply with combined filter effluent turbidity performance standards | 1. 7/1/16
y |  | SEAFAIR ROAD AND WATER COMPANY | 51277 |  |  | 1 | other | 45341 Mar Vista Drive MENDOCINO, CA 95460 | n | n | y | 31 | Monthly / annual flat rate; overage charge if people go over 7,500 gallons per month, otherwise flat rate | Familiar; lack resources to participate |  | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | Point Cabrillo Drive and Mar Vista in city of Mendocino, near Russian Gulch State Park | Mendocino | North Coast, Region 1 | n | 50 | GW | Wells (7) |  |  | 100-150 | $101 - $150 | a water purification system, | The Company owns and/or maintains 4 active wells, 2 active standby wells, approximately 1-1.5 miles of pipeline, a water purification system, and a 10,000 gallon storage tank. | Adequate | We use surface water/shallow wells so sometimes we have biological contamination | [10 empty] | 1
| y | SEAWOOD ESTATES MUTUAL WATER | 50417 | 1 |  |  | Mutual | P.O. Box 561 (161 Westgate Drive) TRINIDAD, CA 95570 | n | y |  | 23 | Monthly/ Annual Flat Rate | Unfamiliar; interested | [17 empty] | 1 | 1 | 1 |  |  | Humboldt | North Coast, Region 1 | n | 60 | SW | IN - Parvin Creek - raw, Savage Creek - raw |  |  | 100/ residence/ mo | $51 - $100 |  |  |  |  | B | 1. Failure to comply with combined filter effluent turbidity performance standards | 1. 10/21/14
|  | SERENO DEL MAR WATER CO. | 49732 | 1 |  |  | other | [29 empty] | Sonoma | North Coast, Region 1 | n
y | y | SEYMOUR'S MUTUAL WATER SYSTEM | 32321 |  | 1 |  | Mutual | HCR2 Box 4793 TRINITY CENTER, CA 96091 | y | n | y | 28 | monthly/ annual flat rate | Familiar; regular participant |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Seymour's Mountain Ranches Mutual Water System Subdivision | Trinity | North Coast, Region 1 | n | 25 | GW | Springs (3) - raw |  |  | 0-50 | $0 - $50
|  | SHADOW MOUNTAIN MHP | 46037 | 1 |  |  | other | P.O. BOX 11158 SANTA ROSA, CA 95406 |  |  |  | 71 | [24 empty] | Sonoma | North Coast, Region 1 | n | 100 | GW | Wells (3)
|  | SHAMROCK MOBILE HOME PARK | 46037 | 1 |  |  | other | 6418 North Old Redwood Highway SANTA ROSA, CA 95403 |  |  |  | 127 | [24 empty] | Sonoma | North Coast, Region 1 | n | 188 | GW | Well | [8 empty] | 0 | 1. Disinfection by-product monitoring reporting violation for 2010 - 2012 | 1. 3/11/13
y | y | SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | 25493 |  | 1 |  | other | P.O. BOX 732 YREKA, CA 96097 | n | y | y | 24 | monthly/ uniform rate schedule | Unfamiliar; interested |  | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 3 | 0 |  | 2 | [6 empty] | Greenhorn Road and Bennett Drive, Yreka | Siskiyou | North Coast, Region 1 | n | 50 | GW | Well |  |  | 51-100; cost includes association fees also - average is $70 to $79 per month per site | $51 - $100 | [14 empty] | 1
|  | SHASTINA MOBILE ESTATES | 18125 |  | 1 |  | other | [29 empty] | Siskiyou | North Coast, Region 1 | n
y |  | SHORELANDS ROAD & WATER COMPANY | 51277 |  |  | 1 | other | P.O. BOX 722 MENDOCINO, CA 95460 | y | n | y | 47 | monthly/ annual flat rate; In addition we charge by usage as a percentage of the volume costs. | Unfamiliar; interested |  | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | Small subdivision just north of Russian Gulch S.P. off of Point Cabrillo Drive, Fern Drive and Cypress Drive being the main streets. | Mendocino | North Coast, Region 1 | n | 85 | GW | Wells (5) |  |  | 51-100 | $51 - $100
|  | SISKIYOU CO. ROLLING HILLS MWC | 25493 |  | 1 |  | Mutual | 501 ARROYO DR. YREKA, CA 96097 |  |  |  | 95 | [24 empty] | Siskiyou | North Coast, Region 1 | n | 300 | GW | Wells (2) | [8 empty] | A | 1. Total coliform bacteria 2. Total coliform monitoring and reporting violations for 2012 - 2013 | 1. 7/19/2016 2. 2/24/17
| y | SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system) | 18125 |  | 1 |  | City | P. O. BOX 470, Weed, CA 96094 | y | n |  | 58 | Monthly/ Annual Flat Rate | Familiar; infrequent participation | [21 empty] | Weed and CSA 5 | Siskiyou | North Coast, Region 1 | n | 142 | GW | Well |  |  | $0-50 | $0 - $50
y |  | Six Acres Water Company | 37411 |  | 1 |  | Other | 87 Lile Lane CLOVERDALE, CA 95425 |  |  |  | 22 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cloverdale, CA | Sonoma | North Coast, Region 1 | n | 66 | GW | Well | [8 empty] | A | 1. Failure to submit 2014 Annual Report to the Division 2. Inorganic, secondary, nitrate, nitrite, perchlorate, VOC, and SOC chemical monitoring and reporting violations for 2014 & 2015 3. Total coliform monitoring and reporting violation for November 2015 4. Compliance Order No. 02_18_16R_001 5. Total coliform monitoring and reporting violation for july - november 2016 6. Total Coliform MCL violation for April 2017 7. Total Coliform monitoring and reporting violation for October 2013 8. Monitoring and reporting violation for December 2012 | 1. 7/17/16 2. 1/22/16 3. 1/12/16 4. 3/30/17 5. 12/7/16 6. 6/2/17 7. 12/6/13 8. 2/12/13
| y | SMITH RIVER C.S.D. | 42944 | 1 |  |  | CSD | 241 FIRST ST. SMITH RIVER, CA 95567 | y | y |  | 582 | increasing block | Familiar; infrequent participation | Funded | [5 empty] | 1 | [5 empty] | 1 | [7 empty] | 1 | Smith River, CA | Del Norte | North Coast, Region 1 | n | 2569 | GW | Wells (4) |  |  | $0-50; $24 minimum charge, then $1.32 per 100 cubic foot afterwards within 0-2,000 cubic feet; over 2000 = $1.59 per cubic foot. | $0 - $50 | Water is treated with sodium hypochlorite and a sodium silicate additive is used. | The water system is supplied by four 40-foot wells that are approximately 100 feet from Rowdy Creek,upstream from Fred Haight Drive. The district’s total storage capacity is 900,000 gallons. Three main storage tanks have a 600,000-gallon combined storage capacity and five smaller storage tanks, located in proximity to various hill side subdivisions, have a 300,000-gallon combined storage capacity. The water system includes four 40-foot wells, two 225,000-gallon redwood storage tanks, three 100,000- gallon redwood storage tanks, and three smaller tanks that have a combined capacity of 125,000 gallons. There are four 25-horsepower pumps and 35-miles of eight-inch mainline for water distribution. Critical infrastructure needs include the replacement of the wooden storage tanks, secured tank foundations, and the installation of new fire hydrants. Additional main storage capacity is currently being added. According to the prior MSR, 25 miles of piping is made of asbestos cement and is in need of replacement. | Fair condition/ Upgrades planned/ identified
|  | SONOMA COUNTY CSA 41-FITCH MOUNTAIN | 46037 | 1 |  |  | County Dist | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | SONOMA COUNTY CSA 41-FREESTONE | 46037 | 1 |  |  | County Dist | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | SONOMA COUNTY CSA 41-JENNER | 46037 | 1 |  |  | County Dist | [29 empty] | Sonoma | North Coast, Region 1 | n
y |  | SONOMA COUNTY CSA 41-SALMON CREEK | 46037 | 1 |  |  | County Dist | 2300 County Center Drive - Suite B100 SANTA ROSA, CA 95403 | y | y | y | 99 | Increasing block (graduated) rate schedule, and monthly/ annual flat rate (sewer) | Familiar; regular participant |  | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 3 | 1 | 1 | 2 | 1 | 3 | 1 | Sonoma County and North Marin County | Sonoma | North Coast, Region 1 | n | 327 | SW | Spring, Well |  |  | 51-100; Sewer only: 2017/2018 Rates: $997/ESD/year rate increase: between 4-5%/year | $51 - $100 |  |  |  |  | 0 | 1. Lead and copper monitoring and reporting violation | 1. 6/9/17 |  |  |  | sewer |  |  |  |  | 1
y |  | SONOMA COUNTY MUTUAL WATER COMPANY | 41389 | 1 |  |  | Mutual | 439 sage court BENICIA,CA 95410 2280 Cazadero Highway CAZADERO, CA 95421 | n | y | y | 20 | monthly/ annual flat rate | Unfamiliar; disinterested |  | 1 | 2 | 1 | 1 | 3 | 3 | 1 | 0 | 0 | 2 | 2 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | Between 2000 Cazadero Hwy and 2420 Cazadero Hwy. | Sonoma | North Coast, Region 1 | n | 40 | GU | Well |  |  | 0-50 | $0 - $50 |  |  |  |  | B | 1. Compliance order No 02_18_17R_008 2. Failure to complay with a Compliance Order May 2013 | 1. 6/23/17 2. 5/28/13
|  | SONOMA COUNTY WATER AGENCY | 46037 | 1 |  |  | County Dist | 2300 County Center Drive - Suite B100 SANTA ROSA, CA 95403 |  |  |  | 99 |  | Familiar; regular participant | Funded | [21 empty] | Sonoma | North Coast, Region 1 | n
|  | SONOMA MOUNTAIN COUNTY WATER DISTRICT | 46037 | 1 |  |  | Water Dist | [29 empty] | Sonoma | North Coast, Region 1 | n
y |  | SOUTH CLOVERDALE WATER COMPANY | 37411 |  | 1 |  | Other | P.O. Box 1111 CLOVERDALE, CA 95425 | n | n | y | 39 | monthly/ annual flat rate | Familiar; not a participant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cloverdale, CA | Sonoma | North Coast, Region 1 | n | 90 | GW | Well |  |  | 51-100 | $51 - $100 |  |  |  |  | C | 1. Compliance order for violation of Section 116555 of the CA Health and Safety Code, which requires each public water system to have a reliable supply of water for its customers. | 1. 10/17/14
|  | SOUTH PARK COUNTY SANITATION DISTRICT | 46037 | 1 |  |  | Sanitary Dist | (MAILING:) 404 AVIATION BLVD., SANTA ROSA, CA 95403 | [28 empty] | Sonoma | North Coast, Region 1 | n
|  | SUMMIT VIEW RANCH MUTUAL WATER CO. | 46037 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | SUNRISE MOUNTAIN MUTUAL WATER COMPANY | 41389 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n
y |  | SUNSET PARK COMMUNITY | 46037 | 1 |  |  | Other | 2963 Santa Rosa Avenue, #D-4 SANTA ROSA, CA 95407 | n | y | y | 55 | Increasing block (graduated) rate schedule; metered, based on City of Santa Rosa rates | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 1 | 2963 Santa Rosa Ave, SR, 95407 | Sonoma | North Coast, Region 1 | n | [5 empty] | 0-50 | $0 - $50
y |  | SURFWOOD MUTUAL WATER CORPORATION | 51277 |  |  | 1 | Mutual | PO Box 166 Mendocino, CA 95640 44901 Baywood Drive MENDOCINO, CA 95460 | n | n | y | 102 | increasing block (graduated) rate schedule | Unfamiliar; lack resources to investigate/participate |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 1 | 1 | 1 | 1 | Surfwood Neighborhood, Mendocino | Mendocino | North Coast, Region 1 | n | 160 | SW | IN, Jack Peter's Creek |  |  | 51-100 | $51 - $100 | filtered prior to distribution | Surface water is collected from Jack Peter’s Creek, stored, and filtered prior to distribution. | Adequate | The Safe Drinking Water Information System lists a number ofmonitoring violations, the most recent occurring in March 2018. The USEPAnotes severalmonitoring and reporting violation dated June 23, 2016 with compliance achieved in November 201633.The Surfwood Mutual Water Corporation noted that SWRCB Compliance Order 02-03-18r-001 was received March 2018 requiring additional water treatment to comply with TTHM and HAA5 maximum contaminate levels. A contract with BWS Municipal Water Group is inprogress (May 2018) to achieve compliance. | C | 1. MCL violations for Total trihalomethane (TTHM) and Haloacetic Acid (HAA5) | 1. 6/23/17
y | y | SWEETWATER SPRINGS CWD - GUERNEVILLE | 45489 | 1 |  |  | Water Dist | P.O. Box 48 GUERNEVILLE, CA 95446 | y | y | y | 2663 | increasing block (graduated) rate schedule; We do bimonthly billing for water use charges and a base (flat) charge. We also have an annual assessment on the County tax bill. Regarding question 30, the current rates are not adequate but we have a plan to make them adequate; it may not be sufficient though. We monitor results annually. | Familiar; not a participant |  | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 2 | 1 | Guerneville, Monte Rio, Rio Nido, Villa Grande, Guernewood Park, Vacation Beach | Sonoma | North Coast, Region 1 | n | 6116 | GW | wells (3) |  |  | 51-100 | $51 - $100 | Manganese and Iron removal is part of our treatment process. Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods. | [12 empty] | Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods.
y | y | SWEETWATER SPRINGS CWD - MONTE RIO | 45489 | 1 |  |  | Water Dist | P.O. Box 48 GUERNEVILLE, CA 95446 | y | y | y | 1064 | increasing block (graduated) rate schedule; We do bimonthly billing for water use charges and a base (flat) charge. We also have an annual assessment on the County tax bill. Regarding question 30, the current rates are not adequate but we have a plan to make them adequate; it may not be sufficient though. We monitor results annually. | Familiar; not a participant |  | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 2 | 1 | Guerneville, Monte Rio, Rio Nido, Villa Grande, Guernewood Park, Vacation Beach | Sonoma | North Coast, Region 1 | n | 3000 | GW | wells (2) |  |  | 51-100 | $51 - $100 | Manganese and Iron removal is part of our treatment process. Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods. | [12 empty] | Recently we had to negotiate treatment and operational processes with the Divsion of Drinking Water regarding a well field that becomes inundated when the Russian River floods.
y |  | TENNANT C.S.D. | 31923 |  | 1 |  | CSD | 13515 TENNANT ROAD MACDOEL, CA 96058 | y | y | y | 97 | Monthly/ annual flat rate | Unfamiliar; disinterested |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | Tennant, CA | Siskiyou | North Coast, Region 1 | n | 94 | GW | Well |  |  | 0-50 | $0 - $50 |  |  |  | we dont have any water problems
|  | TERRACE VIEW WATER SYSTEM | 49726 | 1 |  |  | Other | [29 empty] | Sonoma | North Coast, Region 1 | n
|  | TIMBER COVE COUNTY WATER DISTRICT | 41389 | 1 |  |  | Water Dist | [29 empty] | Sonoma | North Coast, Region 1 | n
y | y | TREASURE CREEK WOODS MWC | 32321 |  | 1 |  | Mutual | HC 2 BOX 3970 TRINITY CENTER, CA 96091 | n | y | y | 36 | monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 0 | 1 | 3 | 3 | 2 | 1 | n/a | 0 | 0 | 2 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 1 | 3 | 2 | We service all subdivisions on the east side of state highway 3 in Coffee Creek, CA | Trinity | North Coast, Region 1 | n | 34 | GW | wells (2) |  |  | $450.00 Annuallly. | $0 - $50 | [10 empty] | sewer
| y | Trinidad Extended Stay | 50417 | 1 |  |  | Other | Humboldt | n | n |  | 50-100 | Included as part of monthly site rental | Unfamiliar; disinterested | [20 empty] | 1 | MidWay RV Park Humboldt county | Humboldt | North Coast, Region 1 | n | 100-250
|  | TRINIDAD, CITY OF | 50417 | 1 |  |  | City | P.O.BOX 1084 TRINIDAD, CA 95570 |  |  |  | 325 |  | Familiar; infrequent participation | Unfunded | [21 empty] | Humboldt | North Coast, Region 1 | n | 1000 | SW | In - Luffenholtz Creek raw water diversion |  |  |  |  | After being treated and chlorinated, water is stored in two redwood tanks, which are carefully monitored to keep the wood wet to avoid warping. Water lines distributetreated water to homes and businesses from the redwood storage tanks. Some out-ofcity residents are served from the line that carries water from the treatment plant to the tanks. These residents may experience a higher chlorine level than customers farther down the line, a problem currently under study. | Potable water for the City system is currently supplied from Luffenholtz Creek, half mile from the coast, and approximately a mile and a half from the City. The pumps located at the infiltration gallery that supply pressure to move water through treatment to the storage tanks were inundated with sediment a few years back. The pumps were rehabilitated, but have never worked as well as expected since their repair. The pumps should be capable of delivering 120 gallons per minute (gpm), but only deliver about 100 gallons per minute. The City of Trinidad has an operations and maintenance program that keeps the storage, treatment, and distribution systems in good condition. The storage tanks are regularly inspected and the steel bands tightened to prevent water losses. The City conducted leak detection testing on the distribution system in 2003 and tested all water meters in 2003. Major leaks detected have been repaired, and poorly functioning water meters are being replaced as funds become available. | Fair condition/ Upgrades planned/ identified | [8 empty] | Currently, the City of Trinidad is comprised of approximately 200 residences, all of which have individual on-site wastewater treatment systems. The maintenance of these systems is a responsibility that falls on the landowner. A large proportion of the existing on-site wastewater disposal systems are more than 20 years old and were either installed prior to permit requirements or prior to permanent record keeping. It is unknown whether systems in and around Trinidad are being maintained or functioning properly. Maintenance of septic systems is very important because it ensures the system is functioning properly, extends the life of the system and helps prevent system failure. Failing septic systems pose a huge problem for homeowners and the City as a whole. The City of Trinidad is in the process of implementing an Onsite Wastewater Treatment System (OWTS) Management Program to provide for sustainable development and better water quality protection, public health and safety and economic stability in our coastal community through improved management of onsite septic systems in Trinidad. | Regulatory - septic
| y | TRINITY CENTER M.W.C. . | 32321 |  | 1 |  | Mutual | P.O. BOX 185 TRINITY CENTER, CA 96091 | n | y |  | 252 | Monthly/ Annual Flat Rate | Unfamiliar; interested | [5 empty] | 1 | 1 |  | 1 |  |  | 1 | 1 | [5 empty] | 1 | 1 |  | Trinity Center, CA | Trinity | North Coast, Region 1 | n | 729 | SW | IN - Swift Creek - raw |  |  | 45 | $0 - $50
y | y | TRINITY CO. W.W. DIST #1 | 28553 |  | 1 |  | County Dist | P.O. BOX 217 HAYFORK, CA 96041 | y | n | y | 535 | Increasing block (graduated) rate schedule; monthly/ annual flat rate | Familiar; regular participant | Funded | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hayfork, CA | Trinity | North Coast, Region 1 | n | 1775 | SW | IN - Big Creek diversion - raw and Hayfork - raw |  |  | Water $29.25 min (with 500 cu ft) Sewer $25.00 per EDU | $51 - $100 | [10 empty] | sewer
y | y | TRINITY KNOLLS MUTUAL WATER COMPANY | 32321 |  | 1 |  | Mutual | P.O. BOX 222 TRINITY CENTER,CA 96091 P.O. BOX 265 TRINITY CENTER, CA 96091 | y | y | n | 65 | Annual flat rate with additional charge for exceeding preset amount of usage | Unfamiliar; lack resources to investigate/participate |  | 0 | 1 | 2 | 2 | 1 | 1 | 2 | 0 | 0 | 3 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 3 | 1 | 3 Subdivisions, KOA Kampground and residences near Trinity Center, CA | Trinity | North Coast, Region 1 | n | 45 | GW | Wells (7) |  |  | 51-100 | $51 - $100 | [14 empty] | 1
|  | TRINITY VILLAGE MUTUAL WATER CO. | 35104 |  | 1 |  | Mutual | P.O. BOX 106 SALYER, CA 95563 |  |  |  | 189 | [24 empty] | Trinity | North Coast, Region 1 | n | 200 | SW | IN - Hawkins Creek - raw, IN, Trinity River - raw - standby
y | y | TULELAKE, CITY OF | 33909 |  | 1 |  | City | 591 Main Street, TULELAKE, CA 96134 | y | n | y | 437 | Monthly/ annual flat rate | Familiar; regular participant | Unfunded | 0 | 0 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | Tulelake, CA | Siskiyou | North Coast, Region 1 | n | 1000 | GW | wells (2) |  |  | 51-100 | $51 - $100 | [10 empty] | sewer |  |  |  |  | 1
|  | Ukiah Valley Sanitation District | 19356 |  | 1 |  | Sanitary Dist | 151 Laws Avenue, Ukiah CA, 95482 | [28 empty] | Mendocino | North Coast, Region 1 | n
y | y | UKIAH, CITY OF | 19356 |  | 1 |  | City | 300 Seminary Avenue UKIAH, CA 95482 | y | y | y | 4781 | Use based, billed monthlyy | Familiar; regular participant | Funded | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 |  | Ukiah, CA | Mendocino | North Coast, Region 1 | n | 16185 | SW | Ranney Collector IN, wells (3) |  |  | 100-150 | $101 - $150 | Because of the nature of ground water in the Ukiah Valley, the only requirement that is necessary at our wells is the addition of a disinfectant to maintain safe potable water in the distribution system. | The City receives project water from Lake Mendocino, groundwater, and surface water. Based onthe 2010 Urban Water Management Plan the City has determined there is sufficient water supply to meet anticipated future demands.The Millview County Water District serves the northern portion of the sphere of influence excep tfor the Brush Street Triangle and the Masonite property. It has sufficient supply to serve its customers through 2015. A recent cease and desist order would reduce available supply by 785 acre-feet annually. The order is being contested, but should it be upheld the District would have difficulty supplying water in 2020 and beyond unless it can purchase additional Lake Mendocino water or find another source.The Willow County Water District has sufficient water to meet future demands for normal, singledry year, and multiple dry year scenarios. | Uncertain water supply | [8 empty] | The City provides wastewater services to about two-thirds of City residents. The other residents receive service from the Ukiah Valley Sanitation District (UVSD). The UVSD also serves the northern and southern portions of the proposed SOI. The City and UVSD have signed a participationagreement whereby the City agrees to provide operation and maintenance of the sewer system andwastewater treatment for the UVSD. For their part, the UVSD agrees to share the costs based onthe number of equivalent sewer service units (ESSUs).The wastewater treatment plant has a capacity of 3.01 million gallons per day (MGD) dry weatherflow, 6.89 MGD average wet weather flow, and 24.5 MGD peak wet weather flow. Recent capitalimprovements, completed in 2010 have expanded the capacity by 2400 ESSUs. Of the additionalcapacity 65 percent was allocated to the District (1,560 ESSUs) and 35 percent to the City (840ESSUs).As of January 31, 2012, the District has 1061 remaining of the 1,560 ESSUs and the City has542.39 remaining of its 840 share. | Adequate | The City maintains a system of surface and underground drainage facilities that drain into OrrsCreek, Gibson Creek, and Doolin Creek and eventually to the Russian River. Since there is nocentral trunk line to collect and convey stormwater to the Russian River, capacity of thestormwater system is unknown. The City has developed a Stormwater Management Plan to reducethe discharge of pollutants from urban runoff into creeks and the Russian River. The planaddresses several areas of concern, public education and outreach, public involvement andparticipation, illicit discharge detection and elimination, construction site runoff control, post-construction stormwater management, and pollution prevention.The Public Involvement andParticipation Programincludes development and implementation of ways to detect and eliminateillicit discharges to the storm sewer system. Construction runoff control could include siltfences and temporary stormwater detention ponds. Post-construction management consists ofpreventative actions such as protecting sensitive areas (e.g., wetlands) or the use of structuralbest management practices such as grassed swales or porous pavement. Pollution preventioninvolves developing and implementing a program for preventing or reducing pollutant runoff frommunicipal operations. Major flood areas include lands adjoining waterways, such as the Russian River and its tributaries in the south Ukiah and Hopland areas. |  |  | 1
|  | Ukiah City WWTP | 19356 |  | 1 |  |  |  | y |  |  |  |  | Unfamiliar; disinterested | [21 empty] | City of Ukiah | Mendocino | North Coast, Region 1 | n | [15 empty] | 1. Admin Civil Liability 2. Admin Civil Liability 3. Unauthorized Discharge and Order Conditions | 1. 6.7.2017 2. 1.24.2018 3.2.28.2019
y |  | Upper Russian River Water Agency | 36346 |  | 1 |  | County Dist | 151 LAWS AVENUE, SUITE D, UKIAH, CA 95482 | y | y | don't know | 101-250 wastewater; 1001-5000 water | monthly/ uniform rate schedule; monthly/ annual flat rate | Familiar; lack resources to participate |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 1 | 2 | 1 | 0 | unincorporated Ukiah and Redwood Valleys | Mendocino | North Coast, Region 1 | n |  | 0-50
| y | VALLEY FORD WATER ASSOCIATION | 46319 | 1 |  |  | Mutual | P.O. BOX 271 VALLEY FORD,CA 94972 | n | y |  | 19 | Uniform Rate Schedule | Unfamiliar; disinterested | [14 empty] | 1 | [6 empty] | Village of Valley Ford | Sonoma | North Coast, Region 1 | n | 40 | GW | Wells (3) |  |  | over $100 | $101 - $150
|  | WADDINGTON W.W. | 38750 | 1 |  |  | other | 4009 GRIZZLY BLUFF RD. FERNDALE, CA 95536 |  |  |  | 24 | [24 empty] | Humboldt | North Coast, Region 1 | n | 75 | GW | Well
|  | WAYSIDE GARDENS MOBILE HOME PARK | 46037 | 1 |  |  | other | 2389 SANTA ROSA AVENUE SANTA ROSA, CA 95407 |  |  |  | 50 | [24 empty] | Sonoma | North Coast, Region 1 | n | 75 | GW | Wells (2) | [8 empty] | 0 | 1. Tetrachloroethylene monitoring and reporting violation fourth quarter 2013 2. Tetrachloroethylene monitoring and reporting violation first quarter 2013 | 1. 3/17/14 2. 6/11/13
y | y | WEAVERVILLE C.S.D. | 40455 | 1 |  |  | CSD | PO Box 1510 (716 Main St.) WEAVERVILLE, CA 96093 | y | y | y | 1594 | Uniform rate schedule | Familiar; regular participant | Unfunded | 1 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 0 | Weaverville, Douglas City | Trinity | North Coast, Region 1 | n | 3554 | SW | IN - East Weaver Creek - raw, Trinity River - raw, West Weaver Creek - raw |  |  | 0-50 | $0 - $50 |  | We have had issues in the past with Disinfection Byproducts, We have just recently been questioned about the presence of pesticides and fertilizers in the water due to Cannabis grows. | Fair condition/ Upgrades planned/ identified
| y | WEAVERVILLE S.D. | 40455 | 1 |  |  | Sanitary Dist | P.O. Box 1269 (242 Trinity Lake Boulevard) WEAVERVILLE, CA 96094 | y | n |  | 1513 | Monthly/ Annual Flat Rate | Familiar; infrequent participation | Funded | [20 empty] | Weaverville, CA | Trinity | North Coast, Region 1 | n | 3600 |  |  |  |  | $0-50 | $0 - $50
y | y | WEED, CITY OF | 18125 |  | 1 |  | City | P.O. BOX 470 WEED, CA 96094 | y | y | y | 1110 | Increasing block (graduated) rate schedule | Familiar; regular participant | Funded | 1 | 3 | 1 | 1 | 2 | 2 | 1 | 1 |  | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1 | 3 |  | Weed, CA | Siskiyou | North Coast, Region 1 | n | 2963 | GW | Springs, Beaughan, wells (3) |  |  | 51-100 | $51 - $100 |  | On June 29, 2017 the City of Weed filed a complaint (COMP-#23422) to the Division of Water Rights and State Water Resources Control Board requesting assistance in addressing a dispute between the City of Weed and Roseburg Forest Products regarding the rights to 2.0 cfs of water from Beaughan Springs in the Shasta River basin. As an independent citizen group, Water for Citizens of Weed, California, we would like to file this complementary complaint in support of the City’s complaint and to provide some additional background and information. The Parent Complaint Number is COMP-23422 submitted 6/29/17. The child Complaint Number is COMP-23423 for your reference. | Uncertain water supply |  | 0 | 1. Total coliform monitoring and reporting violations | 2017-02-24 |  |  |  | sewer | [5 empty] | 1
y | y | WEOTT C.S.D. | 33438 |  | 1 |  | CSD | P.O. BOX 218 WEOTT, CA 95571 | y | y | y | 128 | There is a monthly base rate that comes with a given volume of water that is included with the base rate. If usage exceeds this volume there is a standard charge for each volume of overage (or excessive use) unit. The overage unit is 150 cubic feet. So, for each 150 ft^3 feet of water beyond the base rate allotment, a standard charge per unit is added to the monthly base rate. Hopefully that made sense. | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 1 | 0 | Weott , CA 95571 + one state park campground located in close proximity to Weott | Humboldt | North Coast, Region 1 | n | 364 | SW | IN - A Line, Mill Creek raw, B Line - Unnarmed Creek raw |  |  | 100-150; If there are no water usage overages, the average bill for combined water and wastewater is roughly $104. | $101 - $150 | The springs flow by gravity through two separate treatment and distribution systems – Line A and Line B. Line A has a treatment capacity of 37.7 gpm at the maximum allowable filter loading rate, and Line B has a treatment capacity of 47.7 gpm. Each treatment train has two pressure filters in series. Sodium hypchlorite is injected following filtration. Interties exist between the two systems within the distribution system. Treatment capacity totals approximately 85.4 gpm (0.123 MGD) and is therefore more limiting than source capacity. | WCSD’s water system consists of two surface water sources located across the Eel River and south of Bull Creek. The springs located on Mill Creek are permitted to produce 80 gpm, and the springs located on Corner and Deck Creek are permitted to produce 60 gpm. The springs flow by gravity to two treatment trains – the Mill Creek springs provide water to Line A, while the other springs provide water to Line B. The total rated capacity of these sources is approximately 0.202 MGD. Weott CSD’s water system is in fair condition and has historically suffered supply problems during summer months. The District has installed meters on all service connections, addressed some severe leaks in the system, and adjusted filter operations, such that the treatment plant can operate within the regulatory constraints. The District operates two pressure zones, each served by separate storage and distribution systems. Water storage consists of two tanks: a 79,000 gallon concrete tank and a new 90,000 bolted steel tank. One booster station is in operation to boost Line A following filtration to storage. The distribution system consists of approximately three miles of PVC, steel, and aluminum pipe varying in size from 3 inches to 4 inches. | Fair condition/ Upgrades planned/ identified | No, nothing unusual. Turbidity, especially seasonally, is a frustrating issue at times but that is about it and that is not unusual around here. | B | 1. Failure to monitor for coliform 2. Failure to comply with combined filter effluent turbidity performance standards | 1. 3/7/2013 2. 10/21/14 |  |  |  |  | “The Weott CSD’s wastewater collection system incorporates gravity mains and one lift station that direct wastewater to a community septic tank where preliminary treatment occurs. From here, raw wastewater flows through a recirculation tank and pea gravel filter, a chlorine contact basin, and dechlorination facilities. Disposal facilities consist of both a community leachfield and direct discharge to the South Fork Eel River, although the direct discharge disposal is not currently used. Sludge is dewatered and transported to the Humboldt County solid waste transfer station for landfill disposal. “The Weott CSD currently provides wastewater service to most areas within its service boundaries. The system currently has approximately 134 residential connections, and flows currently range between 14,000 gpd during dry weather and 30,000 gpd during wet weather. The facility has a permitted dry weather capacity of 30,000 gpd, and is therefore operating at approximately 47 percent of design capacity.” The wastewater treatment system was constructed between 1989 and 1991 and system improvements were made in 2000 under a USDA grant that included improvements to the lift station, chlorination/dechlorination equipment, and the gravel filter distribution piping. The system currently is operating well within its design capacity, and no system upgrades are planned other than typical maintenance. | Good condition
|  | WENDELL WATER COMPANY (PUC) | 52396 |  |  | 1 | Public Utility | [29 empty] | Sonoma | North Coast, Region 1 | n
y |  | WEST PARK PROPERTIES | 26544 |  | 1 |  | other | P.O. Box 1902 CRESCENT CITY,CA 95531 2051 NORTHCREST DR. SPACE 35 CRESCENT CITY, CA 95531 |  |  |  | 42 | [23 empty] | 2051 Northcrest Dr. Crescent City Ca. | Del Norte | North Coast, Region 1 | n | 112 | GW | Well
y | y | WEST WATER COMPANY (PUC) | 37411 |  | 1 |  | Public Utility | 335 ELSE WAY CLOVERDALE, CA 95425 | y | y | y | 13 | some metered and some flat | Unfamiliar; lack resources to investigate/participate |  | 0 | 0 | n/a | n/a | 3 | 3 | 3 | 3 | n/a | 3 | 3 | 3 | 3 | 3 |  | 1 | 3 | 0 | 3 | 3 | West's tract | Sonoma | North Coast, Region 1 | n | 40 | GW | Well |  |  | 51-100 | $51 - $100 |  | Need help searching for funding for system upgrades to become "compliant" | Fair condition/ Upgrades planned/ identified
|  | WESTERN MOBILE HOME PARK | 29250 |  | 1 |  | other | 871 38TH AVENUE SANTA CRUZ, CA 95062 |  |  |  | 73 | [24 empty] | Sonoma | North Coast, Region 1 | n | 225 | GW | Wells (2) | [8 empty] | C | 1. Cis-1,2-dichloroethylene and trichloroethylene monitoring and reporting violation for second quarter 2014. 2. Trichloroethylene and cis-1,2-dichloroethylene monitoring and reporting violation for the first quarter of 2013 3. Trichloroethylene MCL violation and domestic water supply permit No. 02-18-05P-4900791 violation | 1. 8/27/14 2. 6/11/13 3. 11/13/13
y | y | WESTHAVEN C.S.D. | 50417 | 1 |  |  | CSD | PO BOX 2015 (446 6th Avenue #B) TRINIDAD, CA 95570 | y | y | y | 226 | uniform rate schedule | Familiar; infrequent participation | Funded | 3 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 1 | 0 | 3 | 1 | 1 | 1 | 1 | 2 | 0 | 3 | 1 | Moonstone / Westhaven California - near Trinidad | Humboldt | North Coast, Region 1 | n | 490 | SW | IN - South Branch of Two Creek, raw, Tributary collector - raw, well, raw |  |  | 51-100; water only | $51 - $100 |  | The system is supplied by three small, spring-fed tributaries of Two Creek at the eastern edge of the community and a 100-foot deep well within the residential area. The creek source represents approximately 75% of the total source capacity, with the well accounting for the remaining 25%. During the system-upgrading project in the early 1990s, the District expended considerable resources in efforts to locate additional local water sources. Except for the well, no additional sources that could be developed in an economically feasible manner were located within the District. During this same time, an attempt by the District to develop a municipal well just outside the northeast boundary failed due to local political impasse. The District has installed meters on all residential connections recently, which has facilitated the District in identifying leaks and distribution system problems. Aside from inadequate source capacity, no serious deficiencies were identified through the DDW inspection. Many improvements have been made to system through IRWM program. Plans are also underway to upgrade the distribution system’s undersized water mains, increase storage capacity, and further explore additional sources of water. Development that has occurred within Westhaven has benefited from previously approved connections to the Westhaven CSD water system or has been approved with the use of individual onsite water systems. | Good condition | Surface water has very high levels of dissolved organic carbon during rainy weather, and we are on the north coast, hence the DBP issues.
|  | Wildwood Campground | 48563 | 1 |  |  | other | 29700 Highway 20 FORT BRAGG,CA 95437 |  |  |  | 50 | [24 empty] | Mendocino | North Coast, Region 1 | n | 150 | GW | Wells (3)
|  | Willits City WWTP | 32667 |  | 1 |  | City | 300 North Lenore Street, Willits, CA 95490 | [28 empty] | Mendocino | North Coast, Region 1 | n | [14 empty] | C | 1. Water Quality Certification for the Willits Emergency Waterline Replacement Well 2. Water Quality Certification for the Willits groundwater test well project 3. NOV and Transmittal of 3/13 Compliance Evaluation Inspection Report. Deficiencies include: laboratory deficiencies; late Biosolids Report; lack of documentation of calibration; time-paced rather than flow based influent and effluent composite samplers; foaming at discharge point 003. | 1. 3/4/15 2. 6/21/17 3. 4/24/13 |  | The City owns, operates, and maintains a public wastewater system includingwastewater collection infrastructure, the recently upgraded Wastewater Treatment Plant (WWTP), and water reclamation facilities. | Adequate
y |  | WILLITS, CITY OF | 32667 |  | 1 |  | City | 111 EAST COMMERCIAL WILLITS, CA 95490 | y | y | y | 2415 | Monthly/ annual flat rate | Familiar; infrequent participation | Funded | [12 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  | Willits, CA | Mendocino | North Coast, Region 1 | n | 6175 | SW | IN - Morris Reservoir |  |  | 51-100 | $51 - $100 | completely upgraded the Water Treatment Plant in 2015, added a third filter and a 220,000-gallon pre-treatment upflow solids contact clarifier, lined the 3MG main water storage tank in 2016, and replaced 3,400-feetof 10-inchsteel pipe with 12-inchductile iron and C-900pipingin 2009 and 2016(Willits, Nov 2018). | The City owns, operates,and maintains a public water system including water supply facilities, a Water Treatment Plant (WTP), and distribution infrastructure. The City’s water system is classified as a Large Water System because it has more than 500 connections and is under the jurisdiction of the State Water Resources Control Board (SWRCB) Division of Drinking Water.The City’s Water Department is responsible for the water enterprise service. Through an agreement executedin November of 1995, the City provides water and wastewater services to the Sherwood Valley Band of Pomo Indians Rancheria located southwest of the City limits,which includes residential units, a community center, and the Sherwood Valley Casino. This agreement provides for the water needs of up to 50 residential units or their functional equivalent.(LAFCo, 2015)The City’s water supply is a combination of surface water from Davis Creek and groundwater from the Elias Replacement Well. Davis Creek is a tributary to Outlet Creek,which is tributary to the Eel River. The City stores water along Davis Creek at Morris Reservoir with 726 acre-feet(AF) capacity and Centennial Reservoir with 635 AF capacity. The watershed area for Davis Creek upstream from MorrisDam is 4.9square miles (3,136 acres).(LAFCo, 2015; Willits, Nov 2018)The City’s WTP is located adjacent to Morris Dam, has a capacity of 3.3 million gallons per day (MGD),and utilizes alternative filtration technology and an upflow clarifier process to produce treated water.The City has five water storage tanks, with a total capacity of 4.711 million gallons (MG),including: a 3.0 MG tank installed in 1980,a 1.5 MG tank and clear well installed in 1989 (both adjacent to the treatment plant),a 0.125 MG tank on Locust Street installed in 1993,a 0.043 MG tank on Laurel Street installed in 1977,and a 0.043 MG tank on Berry Hill installed in 1980. There are eight pressure zones within the City’s water distribution system.(LAFCo, 2015)The City has taken the following corrective actions to meet drinking water standards: completely upgraded the Water Treatment Plant in 2015, added a third filter and a 220,000-gallon pre-treatment upflow solids contact clarifier, lined the 3MG main water storage tank in 2016, and replaced 3,400-feetof 10-inchsteel pipe with 12-inchductile iron and C-900 pipingin 2009 and 2016(Willits, Nov 2018). On October 17, 2014, the SWRCB issued the City a compliance order which determined that the City did not have a reliable supply of water to serve its customers due to the drought conditions and senior water right demands. The order allowed the City to serve existing customers, but prohibited new service connections. It also required the City to secure a reliable long-term supply of water. This order by the SWRCB was rescinded at the end of November 2014 based on further information provided by City Staff to the SWRCB that addressed theirconcerns.(LAFCo, 2015)On August 9, 2017, the City Council approvedfull-time use of the Elias Replacement Well to supplement the City's surface water supply.Groundwater is now a regular water supply to the City’s water system, instead of being limited toemergency situations.A Source Capacity Analysisprepared for the City by GHD consultants specified a maximum well capacity of 800 gallons per minute (gpm); however, with head-loss, friction, and overcoming system pressure, the well pump is a limiting factor. The City routinely pumps this groundwater well at aproduction rate of 330 gpm and proposes not to exceed a total annual use of 400 AF (131MG).The City is currently evaluating potential enhancements to this groundwater system including changing the configuration and increasing the pump size. The Elias Replacement Welloffers a consistent high quality water source that is not prone to seasonal water quality issues like surface water sources. (Willits, 2017b; Willits, Nov 2018). | Fair condition/ Upgrades planned/ identified |  | C | 1. Exceeded MCL for disinfection byproducts in 2015 2. Failure to comply with MCL for a disinfection byproduct | 1. 8/12/2015 2. 10/8/13 |  |  |  | sewer | The City’s WWTP is located in the northeast corner of the City at the end of Sewer Plant Road via North Lenore Avenue and East Commercial Street and the northerly portion of the treatment plant area is located outside the City limits. The City’s wastewater system includes a sewage collection system consisting of approximately 22-miles of gravity-fedsewer mains ranging in size from 4-inches in diameter to 24-inches in diameterand one lift station and 450 manholes. The WWTP also includes associated reclamation and disposal facilities.From October 1 through May 14, treated wastewater is discharged from Discharge Point 003 to Outlet Creek, downstream of the confluence of Broaddus Creek and Baechtel Creek, consistent with the City’s NPDES permit #CA0023060 from the North Coast Regional Water Quality Control Board (RWQCB), and from May 15 through September,and all other times seasonally appropriate, treated wastewater is recycled via irrigation on adjacent pasture lands (Willits, 2019). | Adequate | Major flood areas include low-lying lands east of Willits.
y |  | WILLOW COUNTY WATER DISTRICT | 19356 |  | 1 |  | Water Dist | 151 LAWS AVENUE UKIAH, CA 95482 | y | n | y | 1070 | uniform rate schedule | Familiar; infrequent participation | Unfunded | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2,760 acres immediately south of Ukiah | Mendocino | North Coast, Region 1 | n | 4200 | GW | Wells (5) |  |  | 51-100 | $51 - $100 |  | The WCWD maintains a storage capacity of 1.348 million gallons in nine storage tanks strategically located throughout the WCWD. It has surface water rights of 2,166 AF and can purchase up to 515 AF from Russian River Flood Control District. Demand in 2010 was 1,301 AF and is expected to increase to 1,904 AF in 2030, assuming there are no conservation measures in place. Total supply from all sources is estimated at 2,681 AF in a normal year and 2,308 AF in an extended dry year. The WCWD supplies water through a number of sources, including wells, surface water, and Lake Mendocino water. The WCWD has surface water rights for 1,440 AFY from November to June and 726 AFY year round through diversion of underflow of the Russian River. The WCWD also contracts with RRFC for 515 AFY. The WCWD has five wells, of which three are used only during dry months. The total capacity of the two well fields is 2,700 gallons per minute. The WCWD does not operate a treatment plant. Domestic water is treated in the pump house at the well site. In addition, there are nine storage tanks with a capacity of 1,348,000 gallons. The WCWD has signed a contract to replace the 100,000-gallon storage tank at Firecrest 1 with a 350,000-gallon tank. When that work is complete, the WCWD will have a storage capacity of 1.598 million gallons. The WCWD works with other water agencies in the Ukiah Valley and maintains an emergency intertie with the City of Ukiah. Cooperation among the water agencies is facilitated by the fact that RRFC, Millview, Calpella, Hopland, Ukiah Valley Sanitation District, and Willow all have offices in the 151 Laws Avenue building. The Ukiah Valley Special Districts Municipal Service Review of 2013 recommended that Willow CWD, Calpella CWD, and Hopland PUD consider a formal consolidations through LAFCO. | Good condition | [11 empty] | 1
y | y | WILLOW CREEK C.S.D. | 32209 |  | 1 |  | CSD | P O BOX 8 WILLOW CREEK, CA 95573 | y | y | n | 912 | monthly/ annual flat rate,;uniform rate schedule | Familiar; infrequent participation | Funded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | Willow Creek, CA | Humboldt | North Coast, Region 1 | n | 1710 | GU | Wells (5) |  |  | 0-50; we have high bills in the summer when persons are using lots of water for irrigation of lawns, gardens and cannabis. | $0 - $50 | The water is chlorinated and treated before it placed into the distribution system. The District monitors chlorination and turbidity 24 hours a day. | The District source of supply is from Willow Creek. It consists of six wells located in the mouth of Willow Creek. Four wells draw water from infiltration galleries in the Willow Creek flood plain acting as a natural filtration system. The District has a pumping capacity of 1.9 million gallons per day. The daily average consumption during peak time is 1.6 million gallons per day. Water storage capacity is 1.1 million gallons. The District’s source of supply consists of six wells located in the mouth of Willow Creek. The Willow Creek CSD operates six production wells. Four wells draw water from infiltration galleries in the Willow Creek, which are believed to be under the influence of surface water, and two wells separate from the infiltration gallery, which may or may not be under the influence of surface water. A new water treatment plant was completed in 2007, and has a design capacity of 2,140 gpm. If run for 23 hours per day, treatment capacity is approximately 2.953 MGD. Total source capacity is 2,610 gpm, or 3.76 MGD. Willow Creek CSD’s water system is generally in good condition, although per capita demand is very high (1,861 gpd/cap) and may be the result of system leaks. Current peak water use is approximately 48% of available production capacity. The new water treatment plant has been designed for 2,140 gpm, approximately 40% greater than existing peak day demands. The District does not have adequate storage capacity and has plans to construct of a new 400,000 gallon storage tank above the new treatment plant and Brannan Mountain Road. | Fair condition/ Upgrades planned/ identified | [8 empty] | Willow Creek has been evaluating alternatives for a community wastewater system for a number of years. Willow Creek’s business center along Highway 299 is in need of a centralized wastewater system due to existing disposal field problems which currently limit development. A preliminary engineering report was prepared for the system in 2008 and additional alternatives are under consideration. The ultimate type, location, and construction schedule for a Willow Creek wastewater treatment plant is dependent upon future funding availability and NCRWQCB permitting requirements. The Willow Creek CSD received a Planning/ Preliminary Design Grant for a community wastewater system for the downtown area of Willow Creek. This grant will allow the community of Willow Creek to determine if a wastewater system is a possibility for the downtown area and help determine more detailed estimated costs. A Draft Environmental Impact Report for the Willow Creek Community Services District Downtown Wastewater Development Project was prepared in June, 2015 (SCH #2015012014) and a Final EIR was certified by the District in September, 2015. | Fair condition/ Upgrades planned/ identified
|  | WILLOWSIDE MUTUAL WATER COMPANY | 42958 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n | 350 | GW | Wells (2)
|  | WILSHIRE HEIGHTS MUTUAL WATER COMPANY | 46037 | 1 |  |  | Mutual | [29 empty] | Sonoma | North Coast, Region 1 | n | [11 empty] | A | 1. MCL Violation for total coliform for December 2016 2. same | 1. 3/7/2017 2. 1/31/17
y |  | WINDSOR, TOWN OF | 39614 | 1 |  |  | City | P.O. BOX 100 WINDSOR, CA 95492 |  |  |  | 8883 |  | Familiar; infrequent participation | Unfunded | [20 empty] | Town of Windsor, Airport Industrial Park and Sonoma County Airport, Mayacama and Shiloh Estates | Sonoma | North Coast, Region 1 | n | 27183 | GW | Purchased, Wells (5) |  |  |  |  | Windsor's water supply is naturally high quality. As a result, only chlorine disinfection is required to meet drinking water standards. The pH of the water is adjusted to protect the Town distribution and home plumbing systems from the natural effects of corrosion. | [6 empty] | 0 | 1. Failure to submit 2015 - 2016 Annual Report as required by General Permit for Storm Water Discharges Associated with Industrial Activities, Windsor Wastewater Treatment Plant, WDOD No. 1 49I020487 | 1. 8/4/2016
y |  | Woods, The (Mendocino) | 39667 | 1 |  |  | Other |  | y | y | y | 109 | Don't charge for water, have sewage fee for each home, standard monthly fee. | Unfamiliar; interested |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | Little River, CA | Mendocino | North Coast, Region 1 | n | 150 | GW | Well |  |  | 57 | $51 - $100 | [10 empty] | sewer
y | y | WOODSIDE RV PARK & CAMPGROUND | 31027 |  | 1 |  | other | 17900 N. HWY 1, FORT BRAGG, CA 95437 | y | n | y | 57 | Trailer park residents are not metered...water use included in space rental. |  |  | 1 | 1 | 1 | 0 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | Woodside RV Park 17900 N Hi. 1 Ft Bragg CA 95437 | Mendocino | North Coast, Region 1 | n | 280 | GW | Wells (5) |  |  | Water and Sewer are included as part of the Monthly Rental rate Per Space. There is currently no breakdowns for what portion of the Monthly rate is for those utilities.
y | y | YREKA, CITY OF | 25493 |  | 1 |  | City | 856 N. MAIN STREET YREKA, CA 96097 | y | y | y | 2993 | flat rate based on meter size with variable usage rates | Unfamiliar; interested |  | 1 | 3 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 |  | Yreka, CA | Siskiyou | North Coast, Region 1 | n | 7290 | SW | IN - Fall Creek Intake Dam A, Well, raw, standby |  |  | 0-50; ~$48 for water alone | $0 - $50 | Water from Fall Creek is chlorinated and filtered before it is delivered to ourcustomers. All water systems using surface water are required to routinely measure the turbidity or "clarity" of the filtered water. Turbidity measurements are needed in order to monitor the effectiveness of the filtration process at removing microbiological contaminants that may be found in surface water. | [6 empty] | D | 1. Notice of Violation of SWRCB General Permit for Storm Water Discharges from Small Municipal Separate Storm Sewer Systems | 2016-07-25 | sewer
y | y | YULUPA MUTUAL WATER COMPANY | 46037 | 1 |  |  | Mutual | P.O. Box 2513 SANTA ROSA, CA 95405 | n | y | y | 59 | monthly/ annual flat rate | Familiar; infrequent participation | Unfunded | 0 | 3 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | Woodside development in rural Sonoma County, | Sonoma | North Coast, Region 1 | n | 200 | GW | wells (3) |  |  | 100-150 | $101 - $150 |  |  |  | Iron and manganese. | [10 empty] | 1
|  |  | 238 | 130 | 101 | 7
|  | Total Systems1 | 100% | 54.62% | 42.44% | 2.941%
1 Some systems that are labelled NC or NP in the SDWIS system are included in this list because they appear or are known to serve small communities in the North Coast.

## DAC Communities
Agency Characteristics
2017/18 Survey Response | 2014 Survey Response | Water/ Wastewater System | Median Household Income (MHI) | DAC | SDAC | EDA
|  |  |  | $38,270 < MHI < $51,026 | MHI < $38,270 | $51,026 < MHI < $54,216
|  | AIRPORT/LARKFIELD/WIKIUP SANITATION ZONE (ALWSZ) | 46037 | 1
y |  | ALBION MUTUAL WATER COMPANY | 39667 | 1
| y | ALDERPOINT COUNTY WATER | 26813 |  | 1
| y | ANCIENT REDWOODS R.V. PARK PWS #120 6011 | 48542 | 1
|  | Anderson Valley Community Services District | 36932
|  | ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | 45489 | 1
|  | ATHENA TERRACE MUTUAL WATER COMPANY | 46037 | 1
|  | Austin Creek Mutual (Springhill) | 41389 | 1
|  | AZALEA GLEN | 50417 | 1
| y | BAR 717 RANCH, INC. (SUMMER CAMP) | 50417 | 1
|  | BEACH CREEK MH PARK | 20346 |  | 1
|  | BENBOW W.C. | 36371 |  | 1
|  | BENNETT RIDGE MUTUAL WATER COMPANY | 46037 | 1
| y | BERTSCH OCEANVIEW CSD | 26544 |  | 1
y | y | BIG LAGOON CSD | 50417 | 1
y | y | BIG LAGOON PARK WATER CO. | 20346 |  | 1
|  | BIG RIVER VISTA MUTUAL WATER COMPANY | 51277 |  |  | 1
y | y | BIG ROCK C.S.D. | 26544 |  | 1
y | y | BLUE LAKE, CITY OF | 49828 | 1
|  | BRAND WATER COMPANY | 46037 | 1
|  | BRANGER MUTUAL WATER COMPANY, INC. | 46037 | 1
|  | Branscomb Mutual Water Company | 32667
y |  | BRICELAND C.S.D. | 37778 |  | 1
| y | BROOKTRAILS TOWNSHIP CSD | 32667 |  | 1
|  | BROOKWOOD MOBILE HOME PARK | 46037 | 1
|  | BUCKTAIL MUTUAL WATER COMPANY | 30000 |  | 1
|  | BUD FINE MWC | 30000 |  | 1
y | y | BURNT RANCH ESTATES Mutual Water Co. | 39167 | 1
y |  | BUTTE MOBILE HOME PARK | 26544 |  | 1
y |  | CAL ORE MOBILE ESTATES | 34000 |  | 1
|  | California American GEYSERVILLE WATER WORKS (PUC) | 46250 | 1
| y | Green Diamond Resource Company - Korbel | 38816 | 1
|  | CALIFORNIA-AMERICAN WATER LARKFIELD (PUC) | 46037 | 1
y | y | CALLAHAN WATER DISTRICT | 44242 | 1
y |  | CALPELLA COUNTY WATER DISTRICT | 19356 |  | 1
| y | CAMP LIAHONA REDWOODS (YOUTH SUMMER CAMP) | 39614 | 1
| y | CAMP ROYANEH | 49886 | 1
|  | CANON MANOR WATER SYSTEM | 46037 | 1
y |  | CASPAR SOUTH SERVICE COMPANY | 46037 | 1
|  | Caspar South Water District | 46037 | 1
y |  | CAZADERO WATER COMPANY, INC. | 49886 | 1
|  | CHINOOK WATER SYSTEM | 27200 |  | 1
|  | Church Tree CSD | 26544
y |  | CITY OF ARCATA | 28277 |  | 1
|  | CITY OF COTATI | 50667 | 1
|  | CITY OF ETNA | 30089 |  | 1
|  | City of Ferndale | 38750 | 1
|  | City of Fortuna WWTP | 49403 | 1
y |  | CITY OF FORTUNA | 49403 | 1
y |  | CITY OF SANTA ROSA | 46037 | 1
|  | COPCO LAKE MWC | 40938 | 1
|  | COVE MOBILE VILLA | 25493
y | y | COVELO C.S.D. | 29167 |  | 1
|  | COVELO MOBILE HOME PARK | 29167 |  | 1
y |  | COVINGTON MILL MWC-DIVISION B | 32321 |  | 1
|  | Creekside Cabins & RV Resort | 45299 | 1
y | y | CRESCENT CITY, CITY OF | 26544 |  | 1
|  | CRIVELLI'S WATER SYSTEM | 27200 |  | 1
| y | DEL NORTE COUNTY COMMUNITY SERVICE AREA | 26544 |  | 1
|  | DELORES LANE WATER SYSTEM | 46037 | 1
|  | Dolphin Isle Marina | 31027
y | y | DORRIS, CITY OF | 31923 |  | 1
|  | Dos Rios Mutual Water Company | 23315
|  | EAST AUSTIN CREEK MUTUAL WATER COMPANY | 49886 | 1
|  | EL CRYSTAL MOBILE HOME PARK | 46037 | 1
|  | EL PORTAL MOBILE ESTATES | 29250 |  | 1
|  | ELK COUNTY WATER DISTRICT | 39667 | 1
|  | EMERALD FOREST | 50417 | 1
| y | END-O-VALLEY MUTUAL WATER COMPANY | 46037 | 1
|  | EUREKA, CITY OF, ELK RIVER WWTP | 20346 |  | 1
y | y | EUREKA, CITY OF | 20346 |  | 1
|  | FERNDALE - DEL ORO WATER CO. | 38750 | 1
y | y | FIELDBROOK GLENDALE C.S.D. | 20346 |  | 1
|  | Forestville Water District | 38792 | 1
| y | FORT BRAGG MUNICIPAL IMP DISTRCT | 31027 |  | 1
|  | Fort Bragg City WWTP | 31027 |  | 1
y | y | FORT BRAGG, CITY OF | 31027 |  | 1
| y | FORT JONES, TOWN OF | 45365 | 1
| y | GARBERVILLE SANITARY DISTRICT | 36371 |  | 1
y |  | GASQUET C.S.D. | 35769 |  | 1
|  | GEYSERVILLE SANITATION ZONE | 46250 | 1
|  | GILL CREEK MUTUAL WATER COMPANY | 46250 | 1
|  | GOLDEN BEAR RV PARK | 27200 |  | 1
|  | GREEN ACRES TRAILER PARK | 31027 |  | 1
y | y | GRENADA SANITARY DISTRICT | 43523 | 1
|  | Gualala Community Services District | 40185 | 1
| y | HAPPY CAMP C.S.D. | 41000 | 1
| y | HAPPY CAMP S.D. | 41000 | 1
|  | HEIGHTS MUTUAL WATER COMPANY | 42958 | 1
| y | HERITAGE HOUSE RESORT AND SURFWOOD MUTUAL WATER CORP. | 31027 |  | 1
y | y | HILLS RANCH MUTUAL WATER COMPANY | 39667 | 1
|  | HILTON MUTUAL WATER COMPANY | 49732 | 1
| y | HOLLAND HEIGHTS MUTUAL WATER COMPANY | 46037 | 1
y | y | HOLLY RANCH VILLAGE | 39667 | 1
y | y | HOPLAND PUBLIC UTILITY DISTRICT | 19356 |  | 1
|  | HORNBROOK C.S.D. | 33000 |  | 1
| y | Hussey Ranch Corporation (HRC) C.S.D. | 26544 |  | 1
y |  | HUCKLEBERRY MUTUAL WATER COMPANY | 35000 |  | 1
y | y | HUMBOLDT BAY MWD | 20346 |  | 1
y | y | HUMBOLDT C.S.D. | 44257 | 1
|  | Humboldt County RID #1, Shelter Cove POTW | 42118 | 1
y | y | HUNTER VALLEY CSD | 27200 |  | 1
y | y | INDIAN CREEK TRAILER PARK | 50313 | 1
|  | IRISH BEACH WATER DISTRICT | 48828 | 1
|  | JACOBY CREEK CSD - combined with City of Arcata | 28277 |  | 1
y | y | JED SMITH HOMEOWNERS ASSN. | 26544 |  | 1
|  | JUNIPER CREEK ESTATES | 45365 | 1
|  | KAMP KLAMATH CORP. | 27200 |  | 1
|  | KLAMATH C.S.D. (Del Norte Community Development) | 27200 |  | 1
|  | KLAMATH CAMPER CORRAL | 27200 |  | 1
|  | KLAMATH RIVER RV PARK | 27200 |  | 1
y |  | LAKE SHASTINA C.S.D | 18125 |  | 1
y | y | LAYTONVILLE COUNTY WATER DISTRICT | 23315 |  | 1
y |  | LEWISTON Community Services District | 30000 |  | 1
|  | LITTLE LAKE MOBILE HOME PARK | 32667 |  | 1
y | y | LOLETA C.S.D. | 46458 | 1
|  | MACDOEL WATERWORKS | 28500
| y | MADRONE MUTUAL WATER COMPANY | 50667 | 1
|  | MAGIC MOUNTAIN MUTUAL WATER COMPANY | 37308 |  | 1
y | y | MANILA COMMUNITY SERVICES DIST. | 38816 | 1
| y | MCCLOUD C.S.D. | 39083 | 1
| y | MARK WEST ACRES MWC | 46037 | 1
| y | MARK WEST MUTUAL WATER CO. | 46037 | 1
y | y | MCKINLEYVILLE C.S.D. | 46708 | 1
y |  | MEADOW ESTATES MUTUAL | 36932 |  | 1
|  | MELITA HEIGHTS MUTUAL WATER COMPANY | 46037 | 1
y | y | MENDOCINO CITY C.S.D. | 51277 |  |  | 1
|  | MENDOCINO COUNTY WATER WORKS DISTRICT NO. II | 40185 | 1
|  | MICHELE MUTUAL WATER COMPANY | 42958 | 1
|  | MILL CREEK M.W.C. | 49403 | 1
|  | MILLVIEW COUNTY WATER DISTRICT | 19356 |  | 1
y | y | MIRANDA C.S.D. | 33438 |  | 1
y |  | MOBILE HOME ESTATES | 46037 | 1
|  | MONTAGUE, CITY OF | 40938 | 1
| y | MONTAGUE WATER CONSERVATION DISTRICT | 40938 | 1
|  | MOONSTONE HEIGHTS MWA | 50417 | 1
|  | MOUNT WESKE ESTATES MUTUAL WATER COMPANY | 39614 | 1
|  | MOUNTAIN VIEW MOBILE ESTATES, LLC | 44604 | 1
y | y | MYERS FLAT M.W.S. INC. | 33438 |  | 1
|  | NEWELL COUNTY WATER DISTRICT | 33909 |  | 1
|  | NOEL HEIGHTS-CAL WATER SERVICE (PUC) | 40469 | 1
y |  | NORTH GUALALA WATER COMPANY | 40185 | 1
|  | NORTH STAR MOBILE HOME PARK | 46037 | 1
|  | NOYO HARBOR DISTRICT | 31027 |  | 1
|  | OAK VALLEY ACRES P.O.A. | 25493 |  | 1
y |  | Odd Fellows Recreation Club | 40469 | 1
| y | ORICK C.S.D. | 47621 | 1
y | y | ORLEANS C.S.D. | 40129 | 1
|  | ORLEANS MUTUAL WATER CO. | 40129 | 1
|  | PACIFIC REEFS WATER DISTRICT | 39667 | 1
|  | PALMER CREEK CSD | 49403 | 1
y |  | PALOMINO ESTATES M.W.C. | 36371 |  | 1
|  | PALOMINO LAKES MUTUAL WATER CO. | 37411 |  | 1
|  | PARK ROYAL MUTUAL WATER | 46037 | 1
|  | PATRICK CREEK COMMUNITY SERVICE DISTRICT | 46708 | 1
| y | PHILLIPSVILLE C.S.D. | 33438 |  | 1
|  | Pine Cove RV Park | 39583 | 1
y |  | PINE GROVE Mobile Home PARK | 26544 |  | 1
y |  | PINE MOUNTAIN MUTUAL WATER CO. | 32667 |  | 1
|  | PLAZA MOBILE HOME PARK | 29250 |  | 1
|  | POINT ARENA WATER WORKS | 40208 | 1
|  | Point Arena WWTP | 40208 | 1
| y | Point Arena Lighthouse Keepers | 40208 | 1
|  | RAINS CREEK WATER DISTRICT | 49732 | 1
|  | RANDAL'S RANCHETTE MUTUAL WATER CO. | 46037 | 1
| y | REDCREST WATER WORKS | 48542 | 1
| y | REDWAY C.S.D. | 37778 |  | 1
y |  | REDWOOD HEIGHTS WATER ASSOCIATION | 49886 | 1
y |  | REDWOOD PARK C.S.D. | 27200 |  | 1
y |  | Reservation Ranch | 42944 | 1
y | y | RESORT IMPRVMT. DIST. #1 | 41140 | 1
|  | White Deer Lodge Water System (formerly Ridge Water System) | 32667 |  | 1
|  | RIDGEWOOD WATER SYSTEM | 32667 |  | 1
|  | RIEBLI MUTUAL WATER COMPANY | 42958 | 1
|  | RINCON VALLEY MOBILE ESTATES | 44390 | 1
y | y | RIO DELL, CITY OF | 47639 | 1
y |  | (Russian) RIVER ESTATES MUTUAL WATER COMPANY | 19356 |  | 1
|  | Riverbend Mobile Home Park | 28277 |  | 1
y | y | RIVERSIDE CSD | 52679 |  |  | 1
|  | ROLLING OAKS ROAD ASSOCIATION | 49726 | 1
|  | ROSELAND MOBILE HOME PARK | 46037 | 1
y | y | RUSH CREEK MUTUAL WATER SYSTEM | 40455 | 1
y |  | RUSSIAN RIVER COUNTY SANITATION DISTRICT | 46037 | 1
| y | RUTH LAKE MARINA AND RECREATION AREA | 25395 |  | 1
| y | SALYER HEIGHTS W.S., INC | 35104 |  | 1
|  | SALYER MUTUAL WC (FORMERLY RIVERVIEW AC) | 35104 |  | 1
| y | SANTA ROSA MOBILE ESTATES | 49306 | 1
y |  | SAWYERS BAR COUNTY WATER DISTRICT | 32500 |  | 1
|  | Scotia CSD | 48542 | 1
y |  | SEAFAIR ROAD AND WATER COMPANY | 51277 |  |  | 1
| y | SEAWOOD ESTATES MUTUAL WATER | 50417 | 1
|  | SEQUOIA WATER COMPANY | 52396 |  |  | 1
|  | SERENO DEL MAR WATER CO. | 49732 | 1
y | y | SEYMOUR'S MUTUAL WATER SYSTEM | 32321 |  | 1
|  | SHADOW MOUNTAIN MHP | 46037 | 1
|  | SHAMROCK MOBILE HOME PARK | 46037 | 1
y | y | SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | 25493 |  | 1
|  | SHASTINA MOBILE ESTATES | 18125 |  | 1
y |  | SHORELANDS ROAD & WATER COMPANY | 51277 |  |  | 1
|  | SISKIYOU CO. ROLLING HILLS MWC | 25493 |  | 1
| y | SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system) | 18125 |  | 1
y |  | Six Acres Water Company | 37411 |  | 1
| y | SMITH RIVER C.S.D. | 42944 | 1
|  | SONOMA COUNTY CSA 41-FITCH MOUNTAIN | 46037 | 1
|  | SONOMA COUNTY CSA 41-FREESTONE | 46037 | 1
|  | SONOMA COUNTY CSA 41-JENNER | 46037 | 1
y |  | SONOMA COUNTY CSA 41-SALMON CREEK | 46037 | 1
y |  | SONOMA COUNTY MUTUAL WATER COMPANY | 41389 | 1
|  | SONOMA COUNTY WATER AGENCY | 46037 | 1
|  | SONOMA MOUNTAIN COUNTY WATER DISTRICT | 46037 | 1
|  | SOUNDS OF THE SEAS W. S. | 50417 | 1
y |  | SOUTH CLOVERDALE WATER COMPANY | 37411 |  | 1
|  | SOUTH PARK COUNTY SANITATION DISTRICT | 46037 | 1
|  | SUMMIT VIEW RANCH MUTUAL WATER CO. | 46037 | 1
|  | SUNRISE MOUNTAIN MUTUAL WATER COMPANY | 41389 | 1
y |  | SUNSET PARK COMMUNITY | 46037 | 1
y |  | SURFWOOD MUTUAL WATER CORPORATION | 51277 |  |  | 1
y | y | SWEETWATER SPRINGS CWD - GUERNEVILLE | 45489 | 1
y | y | SWEETWATER SPRINGS CWD - MONTE RIO | 45489 | 1
|  | SYLVAN HARBOR TRAILER PARK | 50417 | 1
y |  | TENNANT C.S.D. | 31923 |  | 1
|  | TERRACE VIEW WATER SYSTEM | 49726 | 1
|  | TIMBER COVE COUNTY WATER DISTRICT | 41389 | 1
y | y | TREASURE CREEK WOODS MWC | 32321 |  | 1
| y | Trinidad Extended Stay | 50417 | 1
|  | TRINIDAD, CITY OF | 50417 | 1
| y | TRINITY CENTER M.W.C. . | 32321 |  | 1
y | y | TRINITY CO. W.W. DIST #1 | 28553 |  | 1
y | y | TRINITY KNOLLS MUTUAL WATER COMPANY | 32321 |  | 1
|  | TRINITY VILLAGE MUTUAL WATER CO. | 35104 |  | 1
| y | TRIUMPH LIFE CAMP (TLC) YOUTH SUMMER CAMP | 35000 |  | 1
y | y | TULELAKE, CITY OF | 33909 |  | 1
|  | TWIN HILLS MUTUAL WATER COMPANY | 52396 |  |  | 1
|  | Ukiah Valley Sanitation District | 19356 |  | 1
y | y | UKIAH, CITY OF | 19356 |  | 1
|  | Ukiah City WWTP | 19356 |  | 1
y |  | Upper Russian River Water Agency | 36346 |  | 1
| y | VALLEY FORD WATER ASSOCIATION | 46319 | 1
|  | WADDINGTON W.W. | 38750 | 1
|  | WAYSIDE GARDENS MOBILE HOME PARK | 46037 | 1
y | y | WEAVERVILLE C.S.D. | 40455 | 1
| y | WEAVERVILLE S.D. | 40455 | 1
y | y | WEED, CITY OF | 18125 |  | 1
y | y | WEOTT C.S.D. | 33438 |  | 1
|  | WENDELL WATER COMPANY (PUC) | 52396 |  |  | 1
y |  | WEST PARK PROPERTIES | 26544 |  | 1
y | y | WEST WATER COMPANY (PUC) | 37411 |  | 1
|  | WESTERN MOBILE HOME PARK | 29250 |  | 1
y | y | WESTHAVEN C.S.D. | 50417 | 1
|  | Wildwood Campground | 48563 | 1
| y | WILDWOOD RETREAT (WILDWOOD CONSERVATION FOUNDATION) | 45489 | 1
|  | Willits City WWTP | 32667 |  | 1
y |  | WILLITS, CITY OF | 32667 |  | 1
y |  | WILLOW COUNTY WATER DISTRICT | 19356 |  | 1
y | y | WILLOW CREEK C.S.D. | 32209 |  | 1
|  | WILLOWSIDE MUTUAL WATER COMPANY | 42958 | 1
|  | WILSHIRE HEIGHTS MUTUAL WATER COMPANY | 46037 | 1
y |  | WINDSOR, TOWN OF | 39614 | 1
y |  | Woods, The (Mendocino) | 39667 | 1
y | y | WOODSIDE RV PARK & CAMPGROUND | 31027 |  | 1
y | y | YREKA, CITY OF | 25493 |  | 1
y | y | YULUPA MUTUAL WATER COMPANY | 46037 | 1
|  |  | 255 | 141 | 105 | 9
|  | Total Systems | 284 | 55.29% | 36.97% | 3.169%

## "Community" ~ "C" Systems
Agency Characteristics
2017/18 Survey Response | 2014 Survey Response | Water System Type Counts |  |  |  |  | Water/ Wastewater System
|  | C - Community | NC - Non-Community | Not in SDWIS System | NP - Not a Public System | NTNC - Non-transient, non-community
y |  | 1 |  |  |  |  | ALBION MUTUAL WATER COMPANY
| y | 1 |  |  |  |  | ALDERPOINT COUNTY WATER
|  | 1 |  |  |  |  | ALEXANDER VALLEY ACRES WATER COMPANY
|  |  | 1 |  |  |  | Anderson Valley Community Services District
|  |  |  | 1 |  |  | Anderson Valley Community Services District
|  | 1 |  |  |  |  | ARMSTRONG VALLEY-CAL WATER SERVICE (PUC)
|  | 1 |  |  |  |  | ATHENA TERRACE MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | AUSTIN ACRES MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | Austin Creek Mutual (Springhill)
|  | 1 |  |  |  |  | BEACH CREEK MH PARK
|  | 1 |  |  |  |  | BELMONT TERRACE MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | BENBOW W.C.
|  | 1 |  |  |  |  | BENNETT RIDGE MUTUAL WATER COMPANY
| y | 1 |  |  |  |  | BERTSCH OCEANVIEW CSD
y | y | 1 |  |  |  |  | BIG LAGOON CSD
y | y | 1 |  |  |  |  | BIG LAGOON PARK WATER CO.
|  | 1 |  |  |  |  | BIG RIVER VISTA MUTUAL WATER COMPANY
y | y | 1 |  |  |  |  | BIG ROCK C.S.D.
y | y | 1 |  |  |  |  | BLUE LAKE, CITY OF
|  | 1 |  |  |  |  | BLUE SPRUCE MOBILE HOME PARK
|  | 1 |  |  |  |  | BODEGA BAY PUBLIC UTILITY DISTRICT
|  | 1 |  |  |  |  | BODEGA WATER COMPANY
|  | 1 |  |  |  |  | BRAND WATER COMPANY
|  | 1 |  |  |  |  | BRANGER MUTUAL WATER COMPANY, INC.
|  | 1 |  |  |  |  | Branscomb Mutual Water Company
y |  | 1 |  |  |  |  | BRICELAND C.S.D.
| y | 1 |  |  |  |  | BROOKTRAILS TOWNSHIP CSD
|  | 1 |  |  |  |  | BROOKWOOD MOBILE HOME PARK
|  | 1 |  |  |  |  | BUCKTAIL MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | BUD FINE MWC
y | y | 1 |  |  |  |  | BURNT RANCH ESTATES Mutual Water Co.
y |  | 1 |  |  |  |  | BUTTE MOBILE HOME PARK
y |  | 1 |  |  |  |  | CAL ORE MOBILE ESTATES
|  | 1 |  |  |  |  | California American GEYSERVILLE WATER WORKS (PUC)
| y | 1 |  |  |  |  | Green Diamond Resource Company - Korbel
|  | 1 |  |  |  |  | CALIFORNIA-AMERICAN WATER LARKFIELD (PUC)
y | y | 1 |  |  |  |  | CALLAHAN WATER DISTRICT
y |  | 1 |  |  |  |  | CALPELLA COUNTY WATER DISTRICT
|  | 1 |  |  |  |  | CAMP MEEKER WATER SYSTEM
|  | 1 |  |  |  |  | CANON MANOR WATER SYSTEM
y |  | 1 |  |  |  |  | CASPAR SOUTH SERVICE COMPANY
|  |  |  | 1 |  |  | Caspar South Water District
y |  | 1 |  |  |  |  | CAZADERO WATER COMPANY, INC.
|  |  | 1 |  |  |  | CHINOOK RV Resort WATER SYSTEM
|  |  |  | 1 |  |  | Church Tree CSD
y |  | 1 |  |  |  |  | CITY OF ARCATA
|  | 1 |  |  |  |  | CITY OF COTATI
|  | 1 |  |  |  |  | CITY OF ETNA
[5 empty] | 1 |  | City of Ferndale
|  |  |  | 1 |  |  | City of Fortuna WWTP
y |  | 1 |  |  |  |  | CITY OF FORTUNA
y |  | 1 |  |  |  |  | CITY OF ROHNERT PARK
y |  | 1 |  |  |  |  | CITY OF SANTA ROSA
|  | 1 |  |  |  |  | CLEAR CREEK WATER COMPANY
y |  | 1 |  |  |  |  | CLOVERDALE, CITY OF
| y | 1 |  |  |  |  | COLONIAL PARK
|  | 1 |  |  |  |  | COPCO LAKE MWC
|  | 1 |  |  |  |  | COVE MOBILE VILLA
y | y |  |  | 1 |  |  | COVELO C.S.D.
|  | 1 |  |  |  |  | COVELO MOBILE HOME PARK
y |  | 1 |  |  |  |  | COVINGTON MILL MWC-DIVISION B
|  | 1 |  |  |  |  | Creekside Cabins & RV Resort
y | y | 1 |  |  |  |  | CRESCENT CITY, CITY OF
| y |  |  | 1 |  |  | DEL NORTE COUNTY COMMUNITY SERVICE AREA
|  | 1 |  |  |  |  | DELORES LANE WATER SYSTEM
|  | 1 |  |  |  |  | Dolphin Isle Marina
y | y | 1 |  |  |  |  | DORRIS, CITY OF
[5 empty] | 1 |  | Dos Rios Mutual Water Company
|  | 1 |  |  |  |  | DOWNTOWN GRATON MUTUAL WATER SYSTEM
|  |  | 1 |  |  |  | EAST AUSTIN CREEK MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | EL CRYSTAL MOBILE HOME PARK
|  | 1 |  |  |  |  | EL PORTAL MOBILE ESTATES
|  | 1 |  |  |  |  | ELK COUNTY WATER DISTRICT
| y | 1 |  |  |  |  | END-O-VALLEY MUTUAL WATER COMPANY
|  |  |  | 1 |  |  | EUREKA, CITY OF, ELK RIVER WWTP
y | y | 1 |  |  |  |  | EUREKA, CITY OF
|  | 1 |  |  |  |  | FERNDALE - DEL ORO WATER CO.
y | y | 1 |  |  |  |  | FIELDBROOK GLENDALE C.S.D.
|  | 1 |  |  |  |  | FIRCREST MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | Forestville Water District
| y |  |  | 1 |  |  | FORT BRAGG MUNICIPAL IMP DISTRCT
|  |  |  | 1 |  |  | Fort Bragg City WWTP
y | y | 1 |  |  |  |  | FORT BRAGG, CITY OF
| y | 1 |  |  |  |  | FORT JONES, TOWN OF
| y | 1 |  |  |  |  | GARBERVILLE SANITARY DISTRICT
y |  | 1 |  |  |  |  | GASQUET C.S.D.
|  |  |  | 1 |  |  | GEYSERVILLE SANITATION ZONE
|  | 1 |  |  |  |  | GILL CREEK MUTUAL WATER COMPANY
| y |  |  |  | 1 |  | Graton CSD
| y | 1 |  |  |  |  | GRATON MUTUAL (GREEN VALLEY HOA)
y | y | 1 |  |  |  |  | GRENADA SANITARY DISTRICT
[5 empty] | 1 |  | Gualala Community Services District
|  | 1 |  |  |  |  | HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM
| y | 1 |  |  |  |  | HAPPY CAMP C.S.D.
| y |  |  | 1 |  |  | HAPPY CAMP S.D.
|  | 1 |  |  |  |  | HAWKINS WATER CO-CAL WATER SERVICE (PUC)
y |  | 1 |  |  |  |  | HEALDSBURG, CITY OF
|  | 1 |  |  |  |  | HEIGHTS MUTUAL WATER COMPANY
y | y | 1 |  |  |  |  | HILLS RANCH MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | HILTON MUTUAL WATER COMPANY
| y | 1 |  |  |  |  | HOLLAND HEIGHTS MUTUAL WATER COMPANY
y | y | 1 |  |  |  |  | HOLLY RANCH VILLAGE
y | y | 1 |  |  |  |  | HOPLAND PUBLIC UTILITY DISTRICT
|  | 1 |  |  |  |  | HORNBROOK C.S.D.
| y | 1 |  |  |  |  | Hussey Ranch Corporation (HRC) C.S.D.
y |  | 1 |  |  |  |  | HUCKLEBERRY MUTUAL WATER COMPANY
y | y | 1 |  |  |  |  | HUMBOLDT BAY MWD
y | y | 1 |  |  |  |  | HUMBOLDT C.S.D.
|  | 1 |  |  |  |  | Humboldt County RID #1, Shelter Cove POTW
y | y | 1 |  |  |  |  | HUNTER VALLEY CSD
|  | 1 |  |  |  |  | HYDESVILLE CO. W.D.
y | y | 1 |  |  |  |  | INDIAN CREEK TRAILER PARK
|  | 1 |  |  |  |  | IRISH BEACH WATER DISTRICT
|  | 1 |  |  |  |  | JACOBY CREEK CSD - combined with City of Arcata
y | y | 1 |  |  |  |  | JED SMITH HOMEOWNERS ASSN.
|  | 1 |  |  |  |  | JUNIPER CREEK ESTATES
| y | 1 |  |  |  |  | KELLY MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | KLAMATH C.S.D. (Del Norte Community Development)
y |  | 1 |  |  |  |  | LAKE SHASTINA C.S.D
|  | 1 |  |  |  |  | LAKE VIEW MUTUAL WATER CO.
y | y | 1 |  |  |  |  | LAS PALMAS MOBILE HOME PARK
y | y | 1 |  |  |  |  | LAYTONVILLE COUNTY WATER DISTRICT
|  | 1 |  |  |  |  | LEISURE MOBILE HOME PARK
y |  | 1 |  |  |  |  | LEWISTON Community Services District
|  | 1 |  |  |  |  | LITTLE LAKE MOBILE HOME PARK
y | y | 1 |  |  |  |  | LOLETA C.S.D.
|  | 1 |  |  |  |  | LONE PINE MUTUAL WATER COMPANY
|  |  |  | 1 |  |  | MACDOEL WATERWORKS
| y | 1 |  |  |  |  | MADRONE MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | MAGIC MOUNTAIN MUTUAL WATER COMPANY
y | y | 1 |  |  |  |  | MANILA COMMUNITY SERVICES DIST.
| y | 1 |  |  |  |  | MCCLOUD C.S.D.
| y | 1 |  |  |  |  | MARK WEST ACRES MWC
| y | 1 |  |  |  |  | MARK WEST MUTUAL WATER CO.
y | y | 1 |  |  |  |  | MCKINLEYVILLE C.S.D.
y |  | 1 |  |  |  |  | MEADOW ESTATES MUTUAL
|  | 1 |  |  |  |  | MELITA HEIGHTS MUTUAL WATER COMPANY
y | y |  |  |  | 1 |  | MENDOCINO CITY C.S.D.
|  |  |  | 1 |  |  | MENDOCINO COUNTY WATER WORKS DISTRICT NO. II
|  | 1 |  |  |  |  | MICHELE MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | MILL CREEK M.W.C.
|  | 1 |  |  |  |  | MILLVIEW COUNTY WATER DISTRICT
y | y | 1 |  |  |  |  | MIRANDA C.S.D.
y |  | 1 |  |  |  |  | MOBILE HOME ESTATES
|  | 1 |  |  |  |  | MONTAGUE, CITY OF
| y |  |  | 1 |  |  | MONTAGUE WATER CONSERVATION DISTRICT
y |  |  |  | 1 |  |  | Montair Subdivision Homeowners Association
|  | 1 |  |  |  |  | MOONSTONE HEIGHTS MWA
|  |  |  | 1 |  |  | MOUNT WESKE ESTATES MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | MOUNTAIN VIEW MOBILE ESTATES, LLC
y | y | 1 |  |  |  |  | MYERS FLAT M.W.S. INC.
|  | 1 |  |  |  |  | NEWELL COUNTY WATER DISTRICT
|  | 1 |  |  |  |  | NOEL HEIGHTS-CAL WATER SERVICE (PUC)
y |  | 1 |  |  |  |  | NORTH GUALALA WATER COMPANY
|  | 1 |  |  |  |  | NORTH STAR MOBILE HOME PARK
|  | 1 |  |  |  |  | OAK VALLEY ACRES P.O.A.
|  | 1 |  |  |  |  | OCCIDENTAL COMMUNITY SERVICES DISTRICT
[5 empty] | 1 |  | OCCIDENTAL COUNTY SANITATION DISTRICT
y |  | 1 |  |  |  |  | Odd Fellows Recreation Club
| y | 1 |  |  |  |  | ORICK C.S.D.
y | y | 1 |  |  |  |  | ORLEANS C.S.D.
|  | 1 |  |  |  |  | ORLEANS MUTUAL WATER CO.
|  |  | 1 |  |  |  | PACIFIC REEFS WATER DISTRICT
|  | 1 |  |  |  |  | PALMER CREEK CSD
y |  | 1 |  |  |  |  | PALOMINO ESTATES M.W.C.
|  | 1 |  |  |  |  | PALOMINO LAKES MUTUAL WATER CO.
|  | 1 |  |  |  |  | PARK ROYAL MUTUAL WATER
|  |  |  | 1 |  |  | PATRICK CREEK COMMUNITY SERVICE DISTRICT
| y | 1 |  |  |  |  | PHILLIPSVILLE C.S.D.
|  | 1 |  |  |  |  | Pine Cove RV Park
y |  | 1 |  |  |  |  | PINE GROVE Mobile Home PARK
|  | 1 |  |  |  |  | PINE HILL TERRACE MOBILE HOME PARK
y |  | 1 |  |  |  |  | PINE MOUNTAIN MUTUAL WATER CO.
|  | 1 |  |  |  |  | PLAZA MOBILE HOME PARK
|  | 1 |  |  |  |  | POINT ARENA WATER WORKS
|  |  |  | 1 |  |  | Point Arena WWTP
y |  | 1 |  |  |  |  | POINT CABRILLO HIGHLANDS
y | y | 1 |  |  |  |  | POINT OF VIEW MUTUAL WATER CO
|  | 1 |  |  |  |  | RAINS CREEK WATER DISTRICT
|  | 1 |  |  |  |  | RANCHO DEL PARADISO-CAL WATER SVC (PUC)
|  | 1 |  |  |  |  | RANDAL'S RANCHETTE MUTUAL WATER CO.
| y | 1 |  |  |  |  | REDCREST WATER WORKS
| y | 1 |  |  |  |  | REDWAY C.S.D.
y |  | 1 |  |  |  |  | REDWOOD HEIGHTS WATER ASSOCIATION
y |  | 1 |  |  |  |  | REDWOOD PARK C.S.D.
y | y | 1 |  |  |  |  | REDWOOD VALLEY COUNTY WATER DISTRICT
y |  | 1 |  |  |  |  | Reservation Ranch
y | y | 1 |  |  |  |  | RESORT IMPRVMT. DIST. #1
|  | 1 |  |  |  |  | RIDGEWOOD WATER SYSTEM
|  | 1 |  |  |  |  | RIEBLI MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | RINCON VALLEY MOBILE ESTATES
y | y | 1 |  |  |  |  | RIO DELL, CITY OF
y |  | 1 |  |  |  |  | (Russian) RIVER ESTATES MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | Riverbend Mobile Home Park
y | y | 1 |  |  |  |  | RIVERSIDE CSD
|  | 1 |  |  |  |  | ROGINA WATER COMPANY INC.
|  | 1 |  |  |  |  | ROLLING OAKS ROAD ASSOCIATION
|  | 1 |  |  |  |  | ROSELAND MOBILE HOME PARK
y | y | 1 |  |  |  |  | RUSH CREEK MUTUAL WATER SYSTEM
y |  |  |  |  | 1 |  | RUSSIAN RIVER COUNTY SANITATION DISTRICT
|  | 1 |  |  |  |  | RUSSIAN RIVER MUTUAL WATER CO.
| y | 1 |  |  |  |  | SALYER HEIGHTS W.S., INC
|  | 1 |  |  |  |  | SALYER MUTUAL WC (FORMERLY RIVERVIEW AC)
| y | 1 |  |  |  |  | SANTA ROSA MOBILE ESTATES
y |  |  | 1 |  |  |  | SAWYERS BAR COUNTY WATER DISTRICT
|  | 1 |  |  |  |  | Scotia CSD
[5 empty] | 1 |  | SEA RANCH SANITATION ZONE
|  | 1 |  |  |  |  | SEA RANCH WATER COMPANY,THE (PUC)
y |  | 1 |  |  |  |  | SEAFAIR ROAD AND WATER COMPANY
| y | 1 |  |  |  |  | SEAWOOD ESTATES MUTUAL WATER
y | y | 1 |  |  |  |  | SEBASTOPOL, CITY OF
|  | 1 |  |  |  |  | SERENO DEL MAR WATER CO.
y | y | 1 |  |  |  |  | SEYMOUR'S MUTUAL WATER SYSTEM
|  | 1 |  |  |  |  | SHADOW MOUNTAIN MHP
|  | 1 |  |  |  |  | SHAMROCK MOBILE HOME PARK
y | y | 1 |  |  |  |  | SHASTA VIEW HEIGHTS OWNERS ASSOCIATION
|  | 1 |  |  |  |  | SHASTINA MOBILE ESTATES
y |  | 1 |  |  |  |  | SHORELANDS ROAD & WATER COMPANY
|  | 1 |  |  |  |  | SISKIYOU CO. ROLLING HILLS MWC
| y | 1 |  |  |  |  | SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system)
y |  | 1 |  |  |  |  | Six Acres Water Company
| y | 1 |  |  |  |  | SMITH RIVER C.S.D.
|  | 1 |  |  |  |  | SONOMA COUNTY CSA 41-FITCH MOUNTAIN
|  | 1 |  |  |  |  | SONOMA COUNTY CSA 41-FREESTONE
|  | 1 |  |  |  |  | SONOMA COUNTY CSA 41-JENNER
y |  | 1 |  |  |  |  | SONOMA COUNTY CSA 41-SALMON CREEK
y |  | 1 |  |  |  |  | SONOMA COUNTY MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | SONOMA COUNTY WATER AGENCY
|  | 1 |  |  |  |  | SONOMA MOUNTAIN COUNTY WATER DISTRICT
y |  | 1 |  |  |  |  | SOUTH CLOVERDALE WATER COMPANY
|  |  |  | 1 |  |  | SOUTH PARK COUNTY SANITATION DISTRICT
|  |  | 1 |  |  |  | STEWARTS POINT WATER SYSTEM
|  | 1 |  |  |  |  | STONEGATE MOBILE HOME PARK
|  | 1 |  |  |  |  | SUMMIT VIEW RANCH MUTUAL WATER CO.
|  | 1 |  |  |  |  | SUNRISE MOUNTAIN MUTUAL WATER COMPANY
y |  | 1 |  |  |  |  | SUNSET PARK COMMUNITY
y |  | 1 |  |  |  |  | SURFWOOD MUTUAL WATER CORPORATION
y | y | 1 |  |  |  |  | SWEETWATER SPRINGS CWD - GUERNEVILLE
y | y | 1 |  |  |  |  | SWEETWATER SPRINGS CWD - MONTE RIO
y |  | 1 |  |  |  |  | TENNANT C.S.D.
|  | 1 |  |  |  |  | TERRACE VIEW WATER SYSTEM
|  | 1 |  |  |  |  | TIMBER COVE COUNTY WATER DISTRICT
y | y | 1 |  |  |  |  | TREASURE CREEK WOODS MWC
| y | 1 |  |  |  |  | Trinidad Extended Stay
|  | 1 |  |  |  |  | TRINIDAD, CITY OF
| y | 1 |  |  |  |  | TRINITY CENTER M.W.C. .
y | y |  |  |  | 1 |  | TRINITY CO. W.W. DIST #1
y | y | 1 |  |  |  |  | TRINITY KNOLLS MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | TRINITY VILLAGE MUTUAL WATER CO.
y | y | 1 |  |  |  |  | TULELAKE, CITY OF
|  |  |  | 1 |  |  | Ukiah Valley Sanitation District
y | y | 1 |  |  |  |  | UKIAH, CITY OF
|  |  |  | 1 |  |  | Ukiah City WWTP
y |  |  |  | 1 |  |  | Upper Russian River Water Agency
| y | 1 |  |  |  |  | VALLEY FORD WATER ASSOCIATION
|  | 1 |  |  |  |  | VINEHILL VISTA MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | WADDINGTON W.W.
|  | 1 |  |  |  |  | WAYSIDE GARDENS MOBILE HOME PARK
y | y | 1 |  |  |  |  | WEAVERVILLE C.S.D.
| y |  |  | 1 |  |  | WEAVERVILLE S.D.
y | y | 1 |  |  |  |  | WEED, CITY OF
y | y | 1 |  |  |  |  | WEOTT C.S.D.
|  | 1 |  |  |  |  | WENDELL WATER COMPANY (PUC)
y |  | 1 |  |  |  |  | WEST PARK PROPERTIES
y | y | 1 |  |  |  |  | WEST WATER COMPANY (PUC)
|  | 1 |  |  |  |  | WESTERN MOBILE HOME PARK
y | y | 1 |  |  |  |  | WESTHAVEN C.S.D.
|  | 1 |  |  |  |  | WESTPORT COUNTY WATER DISTRICT
|  | 1 |  |  |  |  | Wildwood Campground
|  |  |  | 1 |  |  | Willits City WWTP
y |  | 1 |  |  |  |  | WILLITS, CITY OF
y |  | 1 |  |  |  |  | WILLOW COUNTY WATER DISTRICT
y | y | 1 |  |  |  |  | WILLOW CREEK C.S.D.
|  | 1 |  |  |  |  | WILLOWSIDE MUTUAL WATER COMPANY
|  | 1 |  |  |  |  | WILSHIRE HEIGHTS MUTUAL WATER COMPANY
y |  | 1 |  |  |  |  | WINDSOR, TOWN OF
y |  | 1 |  |  |  |  | Woods, The (Mendocino)
y | y | 1 |  |  |  |  | WOODSIDE RV PARK & CAMPGROUND
y | y | 1 |  |  |  |  | YREKA, CITY OF
y | y | 1 |  |  |  |  | YULUPA MUTUAL WATER COMPANY
|  | 241 | 6 | 24 | 9 | 0 | Total "Community" Systems*
|  | 73.33% | 8.788% | 13.64% | 3.03% | 1.212%
|  | 24 | 6 | 24 | 9 |  | Percentage of "total" systems (280)
* Some systems that are labelled NC or NP in the SDWIS system are included in this list because they appear or are known to serve small communities in the North Coast.

## Affordability Calculations
North Coast Resource Partnership Water and Wastewater System Affordability Analysis
Community Water System | Average Monthly Bill |  |  |  |  | Average value | (MHI) |  | Monthly MHI | Annual MHI | % Monthly MHI |  |  | EPA Affordability Criteria Threshold * |  |  |  | System Financial Capability Assmnt
| Describe Average Monthly Bill | Description | Water | Wastewater | Both |  |  | No billing data |  |  | Water | Wastewater | Both | Water > 2.5% | WW > 2% | Both > 4.5% |  | RI - WW bill as % MHI*, **
[17 empty] | < 1% | 1 - 2% | > 2% | Count
AIRPORT/LARKFIELD/WIKIUP SANITATION ZONE (ALWSZ) | [6 empty] | 46037 | 1 | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
ALBION MUTUAL WATER COMPANY | Average service fees range between $41 and $60 per month. | Average service fees range between $41 and $60 per month. | 50.5 |  |  | 50.5 | 39667 |  | 3305.5833 | 39667 | 1.528% | 0% | 0% | [6 empty] | 1
ALDERPOINT COUNTY WATER |  | 0-50; minimum monthly fee of $40.00 for first 2,000. cu. ft. after that additional usage will be billed according to use at same rate per cubic foot. | 40 |  |  | 40 | 26813 |  | 2234.4167 | 26813 | 1.79% | 0% | 0% | [6 empty] | 1
ALEXANDER VALLEY ACRES WATER COMPANY | [6 empty] | 57639 | 1 | 4803.25 | 57639 | 0% | 0% | 0% | [6 empty] | 1
ANCIENT REDWOODS R.V. PARK PWS #120 6011 | [6 empty] | 48542 | 1 | 4045.1667 | 48542 | 0% | 0% | 0% | [6 empty] | 1
Anderson Valley Community Services District | [7 empty] | 1 | 3077.6667 | 36932 | 0% | 0% | 0% | [6 empty] | 1
ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | [6 empty] | 45489 | 1 | 3790.75 | 45489 | 0% | 0% | 0% | [6 empty] | 1
ATHENA TERRACE MUTUAL WATER COMPANY | [6 empty] | 46037 | 1 | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
AUSTIN ACRES MUTUAL WATER COMPANY | [6 empty] | 58333 | 1 | 4861.0833 | 58333 | 0% | 0% | 0% | [6 empty] | 1
Austin Creek Mutual (Springhill) | [6 empty] | 41389 | 1 | 3449.0833 | 41389 | 0% | 0% | 0% | [6 empty] | 1
AZALEA GLEN | [6 empty] | 50417 | 1 | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
BAR 717 RANCH, INC. (SUMMER CAMP) | [6 empty] | 50417 | 1 | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
BEACH CREEK MH PARK | [6 empty] | 20346 | 1 | 1695.5 | 20346 | 0% | 0% | 0% | [6 empty] | 1
BELMONT TERRACE MUTUAL WATER COMPANY | [6 empty] | 99141 | 1 | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
BENBOW W.C. | [6 empty] | 36371 | 1 | 3030.9167 | 36371 | 0% | 0% | 0% | [6 empty] | 1
BENNETT RIDGE MUTUAL WATER COMPANY | [6 empty] | 46037 | 1 | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
BERTSCH OCEANVIEW CSD |  | $0-50; Bertsch Ocreanview's monthly service fee: $9.75. They contract with Crescent City, which sells water for a minimum monthly cost of $12.30 for 0-500 cubic feet, plus $1.07 for each additional cubic foot. | 22.05 |  |  | 22.05 | 26544 |  | 2212 | 26544 | 0.9968% | 0% | 0% | [6 empty] | 1
BIG LAGOON CSD | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 50417 |  | 4201.4167 | 50417 | 1.797% | 0% | 0% | [6 empty] | 1
BIG LAGOON PARK WATER CO. | 0-50 | 0-50 | 25 |  |  | 25 | 20346 |  | 1695.5 | 20346 | 1.474% | 0% | 0% | [6 empty] | 1
BIG RIVER VISTA MUTUAL WATER COMPANY | Average service fees range between $81 and $100 per month. | Average service fees range between $81 and $100 per month. | 90.5 |  |  | 90.5 | 51277 |  | 4273.0833 | 51277 | 2.118% | 0% | 0% | [6 empty] | 1
BIG ROCK C.S.D. | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 26544 |  | 2212 | 26544 | 3.413% | 0% | 0% | 1 | [5 empty] | 1
BLUE LAKE, CITY OF | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 49828 |  | 4152.3333 | 49828 | 0% | 0% | 1.818% | [6 empty] | 1
BLUE SPRUCE MOBILE HOME PARK | [6 empty] | 64612 | 1 | 5384.3333 | 64612 | 0% | 0% | 0% | [6 empty] | 1
BODEGA BAY PUBLIC UTILITY DISTRICT | [6 empty] | 85526 | 1 | 7127.1667 | 85526 | 0% | 0% | 0% | [6 empty] | 1
BODEGA WATER COMPANY | [6 empty] | 85526 | 1 | 7127.1667 | 85526 | 0% | 0% | 0% | [6 empty] | 1
BRAND WATER COMPANY | [6 empty] | 46037 | 1 | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
BRANGER MUTUAL WATER COMPANY, INC. | [6 empty] | 46037 | 1 | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
Branscomb Mutual Water Company | Average service fees range between $61 and $80 per month. | Average service fees range between $61 and $80 per month. | [5 empty] | 1 | 2722.25 | 32667 | 0% | 0% | 0% | [6 empty] | 1
BRICELAND C.S.D. | 0-50 | 0-50 | 25 |  |  | 25 | 37778 |  | 3148.1667 | 37778 | 0.7941% | 0% | 0% | [6 empty] | 1
BROOKTRAILS TOWNSHIP CSD | [6 empty] | 32667 | 1 | 2722.25 | 32667 | 0% | 0% | 0% | [6 empty] | 1
BROOKWOOD MOBILE HOME PARK | [6 empty] | 46037 | 1 | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
BUCHER WATER COMPANY | [6 empty] | 57639 | 1 | 4803.25 | 57639 | 0% | 0% | 0% | [6 empty] | 1
BUCKTAIL MUTUAL WATER COMPANY |  | Annual rate: $368/12 = $30.67 | 30.67 |  |  | 30.67 | 30000 |  | 2500 | 30000 | 1.227% | 0% | 0% | [6 empty] | 1
BUD FINE MWC | [6 empty] | 30000 | 1 | 2500 | 30000 | 0% | 0% | 0% | [6 empty] | 1
BURNT RANCH ESTATES Mutual Water Co. | 0-50 | 0-50 | 25 |  |  | 25 | 39167 |  | 3263.9167 | 39167 | 0.766% | 0% | 0% | [6 empty] | 1
BUTTE MOBILE HOME PARK | 0-50 | 0-50 | 25 |  |  | 25 | 26544 |  | 2212 | 26544 | 1.13% | 0% | 0% | [6 empty] | 1
CAL ORE MOBILE ESTATES | [6 empty] | 34000 |  | 2833.3333 | 34000 | 0% | 0% | 0% | [6 empty] | 1
California American GEYSERVILLE WATER WORKS (PUC) | [8 empty] | 3854.1667 | 46250 | 0% | 0% | 0% | [6 empty] | 1
Green Diamond Resource Company - Korbel |  | private system |  |  |  |  | 38816 |  | 3234.6667 | 38816 | 0% | 0% | 0% | [6 empty] | 1
CALIFORNIA-AMERICAN WATER LARKFIELD (PUC) | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
CALLAHAN WATER DISTRICT | 0-50 | 0-50 | 25 |  |  | 25 | 44242 |  | 3686.8333 | 44242 | 0.6781% | 0% | 0% | [6 empty] | 1
CALPELLA COUNTY WATER DISTRICT | 100-150 | 100-150 |  |  | 125 | 125 | 19356 |  | 1613 | 19356 | 0% | 0% | 7.75% |  |  | 1 |  |  |  | 1
CAMP LIAHONA REDWOODS (YOUTH SUMMER CAMP) |  | N/A, summer camp |  |  |  |  | 39614 |  | 3301.1667 | 39614 | 0% | 0% | 0% | [6 empty] | 1
CAMP MEEKER WATER SYSTEM | [6 empty] | 70714 |  | 5892.8333 | 70714 | 0% | 0% | 0% | [6 empty] | 1
CAMP ROYANEH | [6 empty] | 49886 |  | 4157.1667 | 49886 | 0% | 0% | 0% | [6 empty] | 1
CANON MANOR WATER SYSTEM | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
CASPAR SOUTH SERVICE COMPANY | 100-150 | 100-150 | 125 |  |  | 125 | 46037 |  | 3836.4167 | 46037 | 3.258% | 0% | 0% | 1 | [5 empty] | 1
Caspar South Water District | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
CAZADERO WATER COMPANY, INC. | 0-50 | 0-50 | 25 |  |  | 25 | 49886 |  | 4157.1667 | 49886 | 0.6014% | 0% | 0% | [6 empty] | 1
CHINOOK WATER SYSTEM | [6 empty] | 27200 |  | 2266.6667 | 27200 | 0% | 0% | 0% | [6 empty] | 1
Church Tree CSD | 37.49 | 37.49 | 37.49 |  |  | 37.49 |  |  | 2212 | 26544 | 1.695% | 0% | 0% | [6 empty] | 1
CITY OF ARCATA | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 28277 |  | 2356.4167 | 28277 | 0% | 0% | 3.204% | [6 empty] | 1
CITY OF COTATI | [6 empty] | 50667 |  | 4222.25 | 50667 | 0% | 0% | 0% | [6 empty] | 1
CITY OF ETNA | [6 empty] | 30089 |  | 2507.4167 | 30089 | 0% | 0% | 0% | [6 empty] | 1
City of Ferndale | [8 empty] | 3229.1667 | 38750 | 0% | 0% | 0% | [6 empty] | 1
City of Fortuna WWTP | [8 empty] | 4116.9167 | 49403 | 0% | 0% | 0% | [6 empty] | 1
CITY OF FORTUNA | 100-150 | 100-150 |  |  | 125 | 125 | 49403 |  | 4116.9167 | 49403 | 0% | 0% | 3.036% | [6 empty] | 1
CITY OF ROHNERT PARK | 100-150 | 100-150 |  |  | 125 | 125 | 71576 |  | 5964.6667 | 71576 | 0% | 0% | 2.096% | [6 empty] | 1
CITY OF SANTA ROSA | 100-150 | 100-150 |  |  | 125 | 125 | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 3.258% | [6 empty] | 1
CLEAR CREEK WATER COMPANY | [6 empty] | 63229 |  | 5269.0833 | 63229 | 0% | 0% | 0% | [6 empty] | 1
CLOVERDALE, CITY OF | 100-150 | 100-150 |  |  | 125 | 125 | 63229 |  | 5269.0833 | 63229 | 0% | 0% | 2.372% | [6 empty] | 1
COLONIAL PARK |  | 0-50 |  |  |  | 25 | 57639 |  | 4803.25 | 57639 | 0% | 0% | 0% | [6 empty] | 1
COPCO LAKE MWC | [6 empty] | 40938 |  | 3411.5 | 40938 | 0% | 0% | 0% | [6 empty] | 1
COVE MOBILE VILLA | [8 empty] | 2124.4167 | 25493 | 0% | 0% | 0% | [6 empty] | 1
COVELO C.S.D. | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 29167 |  | 2430.5833 | 29167 | 0% | 0% | 3.106% | [6 empty] | 1
COVELO MOBILE HOME PARK | [6 empty] | 29167 |  | 2430.5833 | 29167 | 0% | 0% | 0% | [6 empty] | 1
COVINGTON MILL MWC-DIVISION B | 0-50 | 0-50 | 25 |  |  | 25 | 32321 |  | 2693.4167 | 32321 | 0.9282% | 0% | 0% | [6 empty] | 1
Creekside Cabins & RV Resort | [8 empty] | 3774.9167 | 45299 | 0% | 0% | 0% | [6 empty] | 1
CRESCENT CITY, CITY OF | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 26544 |  | 2212 | 26544 | 0% | 0% | 3.413% | [6 empty] | 1
CRIVELLI'S WATER SYSTEM | [6 empty] | 27200 |  | 2266.6667 | 27200 | 0% | 0% | 0% | [6 empty] | 1
DEL NORTE COUNTY COMMUNITY SERVICE AREA |  | $6.50/ month | 6.5 |  |  | 6.5 | 26544 |  | 2212 | 26544 | 0.2939% | 0% | 0% | [6 empty] | 1
DELORES LANE WATER SYSTEM | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
Dolphin Isle Marina | [8 empty] | 2585.5833 | 31027 | 0% | 0% | 0% | [6 empty] | 1
DORRIS, CITY OF | Majority of services Resid water-41.75 month/Resid sewer-18.25 Comm1 water-29.04 Sewer 11.62. We have a few like school, clinic and mill that are a higher rate 51-100 | Majority of services Resid water-41.75 month/Resid sewer-18.25 Comm1 water-29.04 Sewer 11.62. We have a few like school, clinic and mill that are a higher rate 51-100 | 41.75 | 18.25 |  | 60 | 31923 |  | 2660.25 | 31923 | 1.569% | 0.686% | 0% |  |  |  | 1 |  |  | 1
Dos Rios Mutual Water Company | $41 - $80 per month | $41 - $80 per month | 60.5 |  |  | 60.5 |  |  | 1942.9167 | 23315 | 3.114% | 0% | 0% | 1 | [5 empty] | 1
DOWNTOWN GRATON MUTUAL WATER SYSTEM | [6 empty] | 99141 |  | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
EAST AUSTIN CREEK MUTUAL WATER COMPANY | [6 empty] | 49886 |  | 4157.1667 | 49886 | 0% | 0% | 0% | [6 empty] | 1
EL CRYSTAL MOBILE HOME PARK | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
EL PORTAL MOBILE ESTATES | [6 empty] | 29250 |  | 2437.5 | 29250 | 0% | 0% | 0% | [6 empty] | 1
ELK COUNTY WATER DISTRICT | [6 empty] | 39667 |  | 3305.5833 | 39667 | 0% | 0% | 0% | [6 empty] | 1
EMERALD FOREST | [6 empty] | 50417 |  | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
END-O-VALLEY MUTUAL WATER COMPANY |  | $50-100 | 75 |  |  | 75 | 46037 |  | 3836.4167 | 46037 | 1.955% | 0% | 0% | [6 empty] | 1
EUREKA, CITY OF, ELK RIVER WWTP | [8 empty] | 1695.5 | 20346 | 0% | 0% | 0% | [6 empty] | 1
EUREKA, CITY OF | [6 empty] | 20346 |  | 1695.5 | 20346 | 0% | 0% | 0% | [6 empty] | 1
FARMER WATER SYSTEM | [6 empty] | 99141 |  | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
FERNDALE - DEL ORO WATER CO. | wastewater = 66.02/month | wastewater = 66.02/month |  | 66.02 |  | 66.02 | 38750 |  | 3229.1667 | 38750 | 0% | 2.044% | 0% |  | 1 |  |  |  | 1 | 1
FIELDBROOK GLENDALE C.S.D. | Water $45 Wastewater $76 | Water $45 Wastewater $76 | 45 | 76 |  | 121 | 20346 |  | 1695.5 | 20346 | 2.654% | 4.482% | 0% | 1 | 1 |  |  |  | 1 | 1
FIRCREST MUTUAL WATER COMPANY | [6 empty] | 99141 |  | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
Forestville Water District | [6 empty] | 38792 |  | 3232.6667 | 38792 | 0% | 0% | 0% | [6 empty] | 1
FORT BRAGG MUNICIPAL IMP DISTRCT | [6 empty] | 31027 |  | 2585.5833 | 31027 | 0% | 0% | 0% | [6 empty] | 1
Fort Bragg City WWTP | [8 empty] | 2585.5833 | 31027 | 0% | 0% | 0% | [6 empty] | 1
FORT BRAGG, CITY OF | 100-150 | 100-150 |  |  | 125 | 125 | 31027 |  | 2585.5833 | 31027 | 0% | 0% | 4.834% |  |  | 1 |  |  |  | 1
FORT JONES, TOWN OF |  | 35 min./water 15 sewer |  |  | 50 | 50 | 45365 |  | 3780.4167 | 45365 | 0% | 0% | 1.323% | [6 empty] | 1
GARBERVILLE SANITARY DISTRICT |  | residential water - 66.89 residential wastewater - 47.70 Water- Variable Base and Variable Usage base rate is by meter size and usage rate is by amount used. Wastewater - fixed base and variable usage. residential usage based on the months of Jan-Mar. Commercial base rate based on 90% of last years usage and usage rate based on 90% of last months usage for each strength. |  |  |  |  | 36371 |  | 3030.9167 | 36371 | 0% | 0% | 0% | [6 empty] | 1
GASQUET C.S.D. | 0-50 | 0-50 | 25 |  |  | 25 | 35769 |  | 2980.75 | 35769 | 0.8387% | 0% | 0% | [6 empty] | 1
GEYSERVILLE SANITATION ZONE | [6 empty] | 46250 |  | 3854.1667 | 46250 | 0% | 0% | 0% | [6 empty] | 1
GILL CREEK MUTUAL WATER COMPANY | [6 empty] | 46250 |  | 3854.1667 | 46250 | 0% | 0% | 0% | [6 empty] | 1
GOLDEN BEAR RV PARK | [6 empty] | 27200 |  | 2266.6667 | 27200 | 0% | 0% | 0% | [6 empty] | 1
Graton CSD |  | There is a one-time connection fee of $10,352, and an annual fee of $1,574.37. |  |  |  |  | 74355 |  | 6196.25 | 74355 | 0% | 0% | 0% | [6 empty] | 1
GRATON MUTUAL (GREEN VALLEY HOA) |  | $50-100 |  |  |  |  | 71576 |  | 5964.6667 | 71576 | 0% | 0% | 0% | [6 empty] | 1
GREEN ACRES TRAILER PARK | [6 empty] | 31027 |  | 2585.5833 | 31027 | 0% | 0% | 0% | [6 empty] | 1
GRENADA SANITARY DISTRICT | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 43523 |  | 3626.9167 | 43523 | 0% | 0% | 2.082% | [6 empty] | 1
Gualala Community Services District | [8 empty] | 3348.75 | 40185 | 0% | 0% | 0% | [6 empty] | 1
HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM | [6 empty] | 71576 |  | 5964.6667 | 71576 | 0% | 0% | 0% | [6 empty] | 1
HAPPY CAMP C.S.D. |  | 0-50 |  |  |  |  | 41000 |  | 3416.6667 | 41000 | 0% | 0% | 0% | [6 empty] | 1
HAPPY CAMP S.D. |  | 0-50 |  |  |  |  | 41000 |  | 3416.6667 | 41000 | 0% | 0% | 0% | [6 empty] | 1
HAWKINS WATER CO-CAL WATER SERVICE (PUC) | [6 empty] | 61576 |  | 5131.3333 | 61576 | 0% | 0% | 0% | [6 empty] | 1
HEALDSBURG, CITY OF | [6 empty] | 57639 |  | 4803.25 | 57639 | 0% | 0% | 0% | [6 empty] | 1
HEIGHTS MUTUAL WATER COMPANY | [6 empty] | 42958 |  | 3579.8333 | 42958 | 0% | 0% | 0% | [6 empty] | 1
HERITAGE HOUSE RESORT AND SURFWOOD MUTUAL WATER CORP. | [6 empty] | 31027 |  | 2585.5833 | 31027 | 0% | 0% | 0% | [6 empty] | 1
HILLS RANCH MUTUAL WATER COMPANY | Average service fees range between $81 and $100 per month. | Average service fees range between $81 and $100 per month. | 90.5 |  |  | 90.5 | 39667 |  | 3305.5833 | 39667 | 2.738% | 0% | 0% | 1 | [5 empty] | 1
HILTON MUTUAL WATER COMPANY | [6 empty] | 49732 |  | 4144.3333 | 49732 | 0% | 0% | 0% | [6 empty] | 1
HOLLAND HEIGHTS MUTUAL WATER COMPANY |  | $0-50 |  |  |  |  | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
HOLLY RANCH VILLAGE | part of rent | part of rent |  |  |  |  | 39667 |  | 3305.5833 | 39667 | 0% | 0% | 0% | [6 empty] | 1
HOPLAND PUBLIC UTILITY DISTRICT | 100-150 | 100-150 |  |  | 125 | 125 | 19356 |  | 1613 | 19356 | 0% | 0% | 7.75% |  |  | 1 |  |  |  | 1
HORNBROOK C.S.D. | [6 empty] | 33000 |  | 2750 | 33000 | 0% | 0% | 0% | [6 empty] | 1
Hussey Ranch Corporation (HRC) C.S.D. |  | 30 |  |  |  |  | 26544 |  | 2212 | 26544 | 0% | 0% | 0% | [6 empty] | 1
HUCKLEBERRY MUTUAL WATER COMPANY | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 35000 |  | 2916.6667 | 35000 | 2.589% | 0% | 0% | 1 | [5 empty] | 1
HUMBOLDT BAY MWD | 0-50 | 0-50 | 25 |  |  | 25 | 20346 |  | 1695.5 | 20346 | 1.474% | 0% | 0% | [6 empty] | 1
HUMBOLDT C.S.D. | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 44257 |  | 3688.0833 | 44257 | 0% | 0% | 2.047% | [6 empty] | 1
Humboldt County RID #1, Shelter Cove POTW | [6 empty] | 42118 |  | 3509.8333 | 42118 | 0% | 0% | 0% | [6 empty] | 1
HUNTER VALLEY CSD | $16 per month billed annually | $16 per month billed annually | 16 |  |  | 16 | 27200 |  | 2266.6667 | 27200 | 0.7059% | 0% | 0% | [6 empty] | 1
HYDESVILLE CO. W.D. | [6 empty] | 56042 |  | 4670.1667 | 56042 | 0% | 0% | 0% | [6 empty] | 1
INDIAN CREEK TRAILER PARK | 0-50 | 0-50 | 25 |  |  | 25 | 50313 |  | 4192.75 | 50313 | 0.5963% | 0% | 0% | [6 empty] | 1
IRISH BEACH WATER DISTRICT | [6 empty] | 48828 |  | 4069 | 48828 | 0% | 0% | 0% | [6 empty] | 1
JACOBY CREEK CSD - combined with City of Arcata | [6 empty] | 28277 |  | 2356.4167 | 28277 | 0% | 0% | 0% | [6 empty] | 1
JED SMITH HOMEOWNERS ASSN. | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 26544 |  | 2212 | 26544 | 3.413% | 0% | 0% | 1 | [5 empty] | 1
JUNIPER CREEK ESTATES | [6 empty] | 45365 |  | 3780.4167 | 45365 | 0% | 0% | 0% | [6 empty] | 1
KAMP KLAMATH CORP. | [6 empty] | 27200 |  | 2266.6667 | 27200 | 0% | 0% | 0% | [6 empty] | 1
KELLY MUTUAL WATER COMPANY |  | 50-100 |  |  |  |  | 99141 |  | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
KLAMATH C.S.D. (Del Norte Community Development) | 36/month water; 18.40/ month, sewer | 36/month water; 18.40/ month, sewer | 36 | 18.4 |  | 54.4 | 27200 |  | 2266.6667 | 27200 | 1.588% | 0.8118% | 0% |  |  |  | 1 |  |  | 1
KLAMATH CAMPER CORRAL | [6 empty] | 27200 |  | 2266.6667 | 27200 | 0% | 0% | 0% | [6 empty] | 1
KLAMATH RIVER RV PARK | [6 empty] | 27200 |  | 2266.6667 | 27200 | 0% | 0% | 0% | [6 empty] | 1
LAKE SHASTINA C.S.D | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 18125 |  | 1510.4167 | 18125 | 0% | 0% | 4.999% |  |  | 1 |  |  |  | 1
LAKE VIEW MUTUAL WATER CO. | [6 empty] | 60692 |  | 5057.6667 | 60692 | 0% | 0% | 0% | [6 empty] | 1
LAS PALMAS MOBILE HOME PARK |  | did not provide |  |  |  |  | 69732 |  | 5811 | 69732 | 0% | 0% | 0% | [6 empty] | 1
LAYTONVILLE COUNTY WATER DISTRICT | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 23315 |  | 1942.9167 | 23315 | 3.886% | 0% | 0% | 1 | [5 empty] | 1
LEISURE MOBILE HOME PARK | [6 empty] | 54497 |  | 4541.4167 | 54497 | 0% | 0% | 0% | [6 empty] | 1
LEWISTON Community Services District | On average, it's about $46/month for water and $54 for wastewater | On average, it's about $46/month for water and $54 for wastewater | 46 | 54 |  | 100 | 30000 |  | 2500 | 30000 | 1.84% | 2.16% | 0% |  | 1 |  |  |  | 1 | 1
LITTLE LAKE MOBILE HOME PARK | [6 empty] | 32667 |  | 2722.25 | 32667 | 0% | 0% | 0% | [6 empty] | 1
LOLETA C.S.D. | water $45/mo.; wastewater: $47/mo. (569/yr: SFR) | water $45/mo.; wastewater: $47/mo. (569/yr: SFR) |  |  |  | 92 | 46458 |  | 3871.5 | 46458 | 0% | 0% | 0% | [6 empty] | 1
LONE PINE MUTUAL WATER COMPANY | [6 empty] | 99141 |  | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
MACDOEL WATERWORKS | [8 empty] | 2375 | 28500 | 0% | 0% | 0% | [6 empty] | 1
MADRONA MANOR 140330 |  | $0-50 |  |  |  |  | 57639 |  | 4803.25 | 57639 | 0% | 0% | 0% | [6 empty] | 1
MADRONE MUTUAL WATER COMPANY |  | $0-50 |  |  |  |  | 50667 |  | 4222.25 | 50667 | 0% | 0% | 0% | [6 empty] | 1
MAGIC MOUNTAIN MUTUAL WATER COMPANY |  |  |  |  | 75 |  | 37308 |  | 3109 | 37308 | 0% | 0% | 2.412% | [6 empty] | 1
MANILA COMMUNITY SERVICES DIST. | 75 | 75 |  |  |  | 75 | 38816 |  | 3234.6667 | 38816 | 0% | 0% | 0% | [6 empty] | 1
MCCLOUD C.S.D. | [8 empty] | 3256.9167 | 39083 | 0% | 0% | 0% | [6 empty] | 1
MARK WEST ACRES MWC |  | $0-50 |  |  |  |  | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
MARK WEST MUTUAL WATER CO. | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
MCKINLEYVILLE C.S.D. | 100-150 | 100-150 |  |  | 125 | 125 | 46708 |  | 3892.3333 | 46708 | 0% | 0% | 3.211% | [6 empty] | 1
MEADOW ESTATES MUTUAL | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 36932 |  | 3077.6667 | 36932 | 2.453% | 0% | 0% | [6 empty] | 1
MELITA HEIGHTS MUTUAL WATER COMPANY | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
MENDOCINO CITY C.S.D. | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 51277 |  | 4273.0833 | 51277 | 0% | 0% | 1.767% | [6 empty] | 1
MENDOCINO COUNTY WATER WORKS DISTRICT NO. II | [6 empty] | 40185 |  | 3348.75 | 40185 | 0% | 0% | 0% | [6 empty] | 1
MICHELE MUTUAL WATER COMPANY | [6 empty] | 42958 |  | 3579.8333 | 42958 | 0% | 0% | 0% | [6 empty] | 1
MILL CREEK M.W.C. | [6 empty] | 49403 |  | 4116.9167 | 49403 | 0% | 0% | 0% | [6 empty] | 1
MILLVIEW COUNTY WATER DISTRICT | [6 empty] | 19356 |  | 1613 | 19356 | 0% | 0% | 0% | [6 empty] | 1
MIRANDA C.S.D. | 0-50; Sewer - $23 monthly, water $12.00 monthly for basic - extra charges for more than 1200 cubic feet. The District is in the process of determining how much to raise the rates, which should be completed this year. | 0-50; Sewer - $23 monthly, water $12.00 monthly for basic - extra charges for more than 1200 cubic feet. The District is in the process of determining how much to raise the rates, which should be completed this year. | 12 | 23 |  | 35 | 33438 |  | 2786.5 | 33438 | 0.4306% | 0.8254% | 0% |  |  |  | 1 |  |  | 1
MOBILE HOME ESTATES | 0-50 | 0-50 | 25 |  |  | 25 | 46037 |  | 3836.4167 | 46037 | 0.6516% | 0% | 0% | [6 empty] | 1
MONTAGUE, CITY OF | [6 empty] | 40938 |  | 3411.5 | 40938 | 0% | 0% | 0% | [6 empty] | 1
MONTAGUE WATER CONSERVATION DISTRICT |  | $49 per acre/foot; Over $100 |  |  |  |  | 40938 |  | 3411.5 | 40938 | 0% | 0% | 0% | [6 empty] | 1
Montair Subdivision Homeowners Association | Each home is charged a fee of approximately $150 per quarter. This fee goes into many HOA services, including the wastewater treatment facility. | Each home is charged a fee of approximately $150 per quarter. This fee goes into many HOA services, including the wastewater treatment facility. |  | 50 |  | 50 | 54844 |  | 4570.3333 | 54844 | 0% | 1.094% | 0% |  |  |  |  | 1 |  | 1
MOONSTONE HEIGHTS MWA | [6 empty] | 50417 |  | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
MOUNT WESKE ESTATES MUTUAL WATER COMPANY | [6 empty] | 39614 |  | 3301.1667 | 39614 | 0% | 0% | 0% | [6 empty] | 1
MOUNTAIN VIEW MOBILE ESTATES, LLC | [6 empty] | 44604 |  | 3717 | 44604 | 0% | 0% | 0% | [6 empty] | 1
MYERS FLAT M.W.S. INC. | 51-100; There is a base rate of $57.00 and a $8.00 surcharge which equals $65.00 total, excluding excess use charges. We also have an $8 surcharge for the CIP. | 51-100; There is a base rate of $57.00 and a $8.00 surcharge which equals $65.00 total, excluding excess use charges. We also have an $8 surcharge for the CIP. | 73 |  |  | 73 | 33438 |  | 2786.5 | 33438 | 2.62% | 0% | 0% | 1 | [5 empty] | 1
NEVES FAMILY TRUST WATER SYSTEM | [6 empty] | 90179 |  | 7514.9167 | 90179 | 0% | 0% | 0% | [6 empty] | 1
NEWELL COUNTY WATER DISTRICT | [6 empty] | 33909 |  | 2825.75 | 33909 | 0% | 0% | 0% | [6 empty] | 1
NOEL HEIGHTS-CAL WATER SERVICE (PUC) | [6 empty] | 40469 |  | 3372.4167 | 40469 | 0% | 0% | 0% | [6 empty] | 1
NORTH GUALALA WATER COMPANY | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 40185 |  | 3348.75 | 40185 | 2.255% | 0% | 0% | [6 empty] | 1
NORTH STAR MOBILE HOME PARK | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
NOYO HARBOR DISTRICT | [6 empty] | 31027 |  | 2585.5833 | 31027 | 0% | 0% | 0% | [6 empty] | 1
OAK VALLEY ACRES P.O.A. | [6 empty] | 25493 |  | 2124.4167 | 25493 | 0% | 0% | 0% | [6 empty] | 1
OCCIDENTAL COMMUNITY SERVICES DISTRICT | [6 empty] | 69219 |  | 5768.25 | 69219 | 0% | 0% | 0% | [6 empty] | 1
OCCIDENTAL COUNTY SANITATION DISTRICT | [6 empty] | 69219 |  | 5768.25 | 69219 | 0% | 0% | 0% | [6 empty] | 1
Odd Fellows Recreation Club | [6 empty] | 40469 |  | 3372.4167 | 40469 | 0% | 0% | 0% | [6 empty] | 1
ORICK C.S.D. |  | 0-50 |  |  |  |  | 47621 |  | 3968.4167 | 47621 | 0% | 0% | 0% | [6 empty] | 1
ORLEANS C.S.D. | 0-50 | 0-50 | 25 |  |  | 25 | 40129 |  | 3344.0833 | 40129 | 0.7476% | 0% | 0% | [6 empty] | 1
ORLEANS MUTUAL WATER CO. | [6 empty] | 40129 |  | 3344.0833 | 40129 | 0% | 0% | 0% | [6 empty] | 1
PACIFIC REEFS WATER DISTRICT | [6 empty] | 39667 |  | 3305.5833 | 39667 | 0% | 0% | 0% | [6 empty] | 1
PALMER CREEK CSD | [6 empty] | 49403 |  | 4116.9167 | 49403 | 0% | 0% | 0% | [6 empty] | 1
PALOMINO ESTATES M.W.C. | 100-150 | 100-150 | 125 |  |  | 125 | 36371 |  | 3030.9167 | 36371 | 4.124% | 0% | 0% | 1 | [5 empty] | 1
PALOMINO LAKES MUTUAL WATER CO. | [6 empty] | 37411 |  | 3117.5833 | 37411 | 0% | 0% | 0% | [6 empty] | 1
PARK ROYAL MUTUAL WATER | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
PATRICK CREEK COMMUNITY SERVICE DISTRICT | [8 empty] | 3892.3333 | 46708 | 0% | 0% | 0% | [6 empty] | 1
PHILLIPSVILLE C.S.D. |  | $0-50 |  |  |  |  | 33438 |  | 2786.5 | 33438 | 0% | 0% | 0% | [6 empty] | 1
Pine Cove RV Park | [8 empty] | 3298.5833 | 39583 | 0% | 0% | 0% | [6 empty] | 1
PINE GROVE Mobile Home PARK | [6 empty] | 26544 |  | 2212 | 26544 | 0% | 0% | 0% | [6 empty] | 1
PINE HILL TERRACE MOBILE HOME PARK | [6 empty] | 99141 |  | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
PINE MOUNTAIN MUTUAL WATER CO. | 61 - 80 | 61 - 80 | 70.5 |  |  | 70.5 | 32667 |  | 2722.25 | 32667 | 2.59% | 0% | 0% | 1 | [5 empty] | 1
PLAZA MOBILE HOME PARK | [6 empty] | 29250 |  | 2437.5 | 29250 | 0% | 0% | 0% | [6 empty] | 1
POINT ARENA WATER WORKS | [6 empty] | 40208 |  | 3350.6667 | 40208 | 0% | 0% | 0% | [6 empty] | 1
Point Arena WWTP | [6 empty] | 40208 |  | 3350.6667 | 40208 | 0% | 0% | 0% | [6 empty] | 1
Point Arena Lighthouse Keepers | [6 empty] | 40208 |  | 3350.6667 | 40208 | 0% | 0% | 0% | [6 empty] | 1
POINT CABRILLO HIGHLANDS | [6 empty] | 56250 |  | 4687.5 | 56250 | 0% | 0% | 0% | [6 empty] | 1
POINT OF VIEW MUTUAL WATER CO | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 51277 |  | 4273.0833 | 51277 | 1.767% | 0% | 0% | [6 empty] | 1
RAINS CREEK WATER DISTRICT | [6 empty] | 49732 |  | 4144.3333 | 49732 | 0% | 0% | 0% | [6 empty] | 1
RANCHO DEL PARADISO-CAL WATER SVC (PUC) | [6 empty] | 58333 |  | 4861.0833 | 58333 | 0% | 0% | 0% | [6 empty] | 1
RANDAL'S RANCHETTE MUTUAL WATER CO. | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
REDCREST WATER WORKS |  | $0-50 |  |  |  |  | 48542 |  | 4045.1667 | 48542 | 0% | 0% | 0% | [6 empty] | 1
REDWAY C.S.D. |  | $50-100; Res. $60.00 goes by use; Commercial $64. per month and goes up by use. |  |  |  |  | 37778 |  | 3148.1667 | 37778 | 0% | 0% | 0% | [6 empty] | 1
REDWOOD HEIGHTS WATER ASSOCIATION | [6 empty] | 49886 |  | 4157.1667 | 49886 | 0% | 0% | 0% | [6 empty] | 1
REDWOOD PARK C.S.D. | 0-50 | 0-50 |  |  | 25 | 25 | 27200 |  | 2266.6667 | 27200 | 0% | 0% | 1.103% | [6 empty] | 1
REDWOOD VALLEY COUNTY WATER DISTRICT | 0-50 | 0-50 | 25 |  |  | 25 | 60692 |  | 5057.6667 | 60692 | 0.4943% | 0% | 0% | [6 empty] | 1
Reservation Ranch | n/a | n/a |  |  |  |  | 42944 |  | 3578.6667 | 42944 | 0% | 0% | 0% | [6 empty] | 1
RESORT IMPRVMT. DIST. #1 | 100-150 | 100-150 |  |  | 125 | 125 | 41140 |  | 3428.3333 | 41140 | 0% | 0% | 3.646% | [6 empty] | 1
White Deer Lodge Water System (formerly Ridge Water System) | [6 empty] | 32667 |  | 2722.25 | 32667 | 0% | 0% | 0% | [6 empty] | 1
RIDGEWOOD WATER SYSTEM | [6 empty] | 32667 |  | 2722.25 | 32667 | 0% | 0% | 0% | [6 empty] | 1
RIEBLI MUTUAL WATER COMPANY | [6 empty] | 42958 |  | 3579.8333 | 42958 | 0% | 0% | 0% | [6 empty] | 1
RINCON VALLEY MOBILE ESTATES | [6 empty] | 44390 |  | 3699.1667 | 44390 | 0% | 0% | 0% | [6 empty] | 1
RIO DELL, CITY OF | $61.83/month water and $71.39/month sewer | $61.83/month water and $71.39/month sewer | 61.83 | 71.39 |  | 133.22 | 47639 |  | 3969.9167 | 47639 | 1.557% | 1.798% | 0% |  |  |  |  | 1 |  | 1
(Russian) RIVER ESTATES MUTUAL WATER COMPANY | 61-80 | 61-80 |  |  |  | 70.5 | 19356 |  | 1613 | 19356 | 0% | 0% | 0% | [6 empty] | 1
Riverbend Mobile Home Park | [6 empty] | 28277 |  | 2356.4167 | 28277 | 0% | 0% | 0% | [6 empty] | 1
RIVERSIDE CSD | [6 empty] | 52679 |  | 4389.9167 | 52679 | 0% | 0% | 0% | [6 empty] | 1
ROGINA WATER COMPANY INC. | [6 empty] | 73523 |  | 6126.9167 | 73523 | 0% | 0% | 0% | [6 empty] | 1
ROLLING OAKS ROAD ASSOCIATION | [6 empty] | 49726 |  | 4143.8333 | 49726 | 0% | 0% | 0% | [6 empty] | 1
ROSELAND MOBILE HOME PARK | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
RUSH CREEK MUTUAL WATER SYSTEM | 51-100 | 51-100 | 25 |  |  | 75.5 | 40455 |  | 3371.25 | 40455 | 0.7416% | 0% | 0% | [6 empty] | 1
RUSSIAN RIVER COUNTY SANITATION DISTRICT | Property tax charges, $1484 per ESD (1 unit) wastewater only; estimate 100-150 | Property tax charges, $1484 per ESD (1 unit) wastewater only; estimate 100-150 |  | 124 |  | 123.6667 | 46037 |  | 3836.4167 | 46037 | 0% | 3.232% | 0% |  | 1 |  |  |  | 1 | 1
RUSSIAN RIVER MUTUAL WATER CO. | [6 empty] | 57639 |  | 4803.25 | 57639 | 0% | 0% | 0% | [6 empty] | 1
RUTH LAKE MARINA AND RECREATION AREA | [6 empty] | 25395 |  | 2116.25 | 25395 | 0% | 0% | 0% | [6 empty] | 1
SALYER HEIGHTS W.S., INC |  | $180 a year |  |  |  |  | 35104 |  | 2925.3333 | 35104 | 0% | 0% | 0% | [6 empty] | 1
SALYER MUTUAL WC (FORMERLY RIVERVIEW AC) | [6 empty] | 35104 |  | 2925.3333 | 35104 | 0% | 0% | 0% | [6 empty] | 1
SANTA ROSA MOBILE ESTATES | [6 empty] | 49306 |  | 4108.8333 | 49306 | 0% | 0% | 0% | [6 empty] | 1
SAWYERS BAR COUNTY WATER DISTRICT | Over $150 | Over $150 | 151 |  |  | 151 | 32500 |  | 2708.3333 | 32500 | 5.575% | 0% | 0% | 1 | [5 empty] | 1
Scotia CSD | [6 empty] | 48542 |  | 4045.1667 | 48542 | 0% | 0% | 0% | [6 empty] | 1
SEA RANCH SANITATION ZONE | [6 empty] | 62750 |  | 5229.1667 | 62750 | 0% | 0% | 0% | [6 empty] | 1
SEA RANCH WATER COMPANY,THE (PUC) | [6 empty] | 62750 |  | 5229.1667 | 62750 | 0% | 0% | 0% | [6 empty] | 1
SEAFAIR ROAD AND WATER COMPANY | 100-150 | 100-150 | 125 |  |  | 125 | 51277 |  | 4273.0833 | 51277 | 2.925% | 0% | 0% | 1 | [5 empty] | 1
SEAWOOD ESTATES MUTUAL WATER |  | 100/ residence/ mo |  |  |  |  | 50417 |  | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
SEBASTOPOL, CITY OF | 100-150 | 100-150 |  |  | 125 | 125 | 99141 |  | 8261.75 | 99141 | 0% | 0% | 1.513% | [6 empty] | 1
SEQUOIA WATER COMPANY | [6 empty] | 52396 |  | 4366.3333 | 52396 | 0% | 0% | 0% | [6 empty] | 1
SERENO DEL MAR WATER CO. | [6 empty] | 49732 |  | 4144.3333 | 49732 | 0% | 0% | 0% | [6 empty] | 1
SEYMOUR'S MUTUAL WATER SYSTEM | 0-50 | 0-50 | 25 |  |  | 25 | 32321 |  | 2693.4167 | 32321 | 0.9282% | 0% | 0% | [6 empty] | 1
SHADOW MOUNTAIN MHP | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SHAMROCK MOBILE HOME PARK | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | 51-100; cost includes association fees also - average is $70 to $79 per month per site | 51-100; cost includes association fees also - average is $70 to $79 per month per site | 69 |  |  | 69 | 25493 |  | 2124.4167 | 25493 | 3.248% | 0% | 0% | 1 | [5 empty] | 1
SHASTINA MOBILE ESTATES | [6 empty] | 18125 |  | 1510.4167 | 18125 | 0% | 0% | 0% | [6 empty] | 1
SHORELANDS ROAD & WATER COMPANY | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 51277 |  | 4273.0833 | 51277 | 1.767% | 0% | 0% | [6 empty] | 1
SISKIYOU CO. ROLLING HILLS MWC | [6 empty] | 25493 |  | 2124.4167 | 25493 | 0% | 0% | 0% | [6 empty] | 1
SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system) |  | $0-50 |  |  |  |  | 18125 |  | 1510.4167 | 18125 | 0% | 0% | 0% | [6 empty] | 1
Six Acres Water Company | [6 empty] | 37411 |  | 3117.5833 | 37411 | 0% | 0% | 0% | [6 empty] | 1
SMITH RIVER C.S.D. |  | $0-50; $24 minimum charge, then $1.32 per 100 cubic foot afterwards within 0-2,000 cubic feet; over 2000 = $1.59 per cubic foot. |  |  |  |  | 42944 |  | 3578.6667 | 42944 | 0% | 0% | 0% | [6 empty] | 1
SONOMA COUNTY CSA 41-FITCH MOUNTAIN | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SONOMA COUNTY CSA 41-FREESTONE | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SONOMA COUNTY CSA 41-JENNER | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SONOMA COUNTY CSA 41-SALMON CREEK | 51-100; Sewer only: 2017/2018 Rates: $997/ESD/year rate increase: between 4-5%/year | 51-100; Sewer only: 2017/2018 Rates: $997/ESD/year rate increase: between 4-5%/year |  | 100 |  | 100 | 46037 |  | 3836.4167 | 46037 | 0% | 2.607% | 0% |  | 1 |  |  |  | 1 | 1
SONOMA COUNTY MUTUAL WATER COMPANY | 0-50 | 0-50 | 25 |  |  | 25 | 41389 |  | 3449.0833 | 41389 | 0.7248% | 0% | 0% | [6 empty] | 1
SONOMA COUNTY WATER AGENCY | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SONOMA MOUNTAIN COUNTY WATER DISTRICT | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SONOMA WEST HOLDINGS NORTH PLANT | [6 empty] | 99141 |  | 8261.75 | 99141 | 0% | 0% | 0% | [6 empty] | 1
SOUNDS OF THE SEAS W. S. | [6 empty] | 50417 |  | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
SOUTH CLOVERDALE WATER COMPANY | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 37411 |  | 3117.5833 | 37411 | 2.422% | 0% | 0% | [6 empty] | 1
SOUTH PARK COUNTY SANITATION DISTRICT | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
STEWARTS POINT WATER SYSTEM | [6 empty] | 61786 |  | 5148.8333 | 61786 | 0% | 0% | 0% | [6 empty] | 1
STONEGATE MOBILE HOME PARK | [6 empty] | 65516 |  | 5459.6667 | 65516 | 0% | 0% | 0% | [6 empty] | 1
SUMMIT VIEW RANCH MUTUAL WATER CO. | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
SUNRISE MOUNTAIN MUTUAL WATER COMPANY | [6 empty] | 41389 |  | 3449.0833 | 41389 | 0% | 0% | 0% | [6 empty] | 1
SUNSET PARK COMMUNITY | 0-50 | 0-50 | 25 |  |  | 25 | 46037 |  | 3836.4167 | 46037 | 0.6516% | 0% | 0% | [6 empty] | 1
SURFWOOD MUTUAL WATER CORPORATION | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 51277 |  | 4273.0833 | 51277 | 1.767% | 0% | 0% | [6 empty] | 1
SWEETWATER SPRINGS CWD - GUERNEVILLE | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 45489 |  | 3790.75 | 45489 | 1.992% | 0% | 0% | [6 empty] | 1
SWEETWATER SPRINGS CWD - MONTE RIO | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 45489 |  | 3790.75 | 45489 | 1.992% | 0% | 0% | [6 empty] | 1
SYLVAN HARBOR TRAILER PARK | [6 empty] | 50417 |  | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
TENNANT C.S.D. | 0-50 | 0-50 |  |  | 25 | 25 | 31923 |  | 2660.25 | 31923 | 0% | 0% | 0.9398% | [6 empty] | 1
TERRACE VIEW WATER SYSTEM | [6 empty] | 49726 |  | 4143.8333 | 49726 | 0% | 0% | 0% | [6 empty] | 1
TIMBER COVE COUNTY WATER DISTRICT | [6 empty] | 41389 |  | 3449.0833 | 41389 | 0% | 0% | 0% | [6 empty] | 1
TREASURE CREEK WOODS MWC | $450.00 Annuallly. | $450.00 Annuallly. | 37.5 |  |  | 37.5 | 32321 |  | 2693.4167 | 32321 | 1.392% | 0% | 0% | [6 empty] | 1
Trinidad Extended Stay | [6 empty] | 50417 |  | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
TRINIDAD, CITY OF | [6 empty] | 50417 |  | 4201.4167 | 50417 | 0% | 0% | 0% | [6 empty] | 1
TRINITY CENTER M.W.C. . |  | 45 |  |  |  |  | 32321 |  | 2693.4167 | 32321 | 0% | 0% | 0% | [6 empty] | 1
TRINITY CO. W.W. DIST #1 | Water $29.25 min (with 500 cu ft) Sewer $25.00 per EDU | Water $29.25 min (with 500 cu ft) Sewer $25.00 per EDU | 29.25 | 25 |  | 54.25 | 28553 |  | 2379.4167 | 28553 | 1.229% | 1.051% | 0% |  |  |  |  | 1 |  | 1
TRINITY KNOLLS MUTUAL WATER COMPANY | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 32321 |  | 2693.4167 | 32321 | 2.803% | 0% | 0% | 1 | [5 empty] | 1
TRINITY VILLAGE MUTUAL WATER CO. | [6 empty] | 35104 |  | 2925.3333 | 35104 | 0% | 0% | 0% | [6 empty] | 1
TRIUMPH LIFE CAMP (TLC) YOUTH SUMMER CAMP | [6 empty] | 35000 |  | 2916.6667 | 35000 | 0% | 0% | 0% | [6 empty] | 1
TULELAKE, CITY OF | 51-100 | 51-100 |  | 75.5 |  | 75.5 | 33909 |  | 2825.75 | 33909 | 0% | 2.672% | 0% |  | 1 |  |  |  | 1 | 1
TWIN HILLS MUTUAL WATER COMPANY | [6 empty] | 52396 |  | 4366.3333 | 52396 | 0% | 0% | 0% | [6 empty] | 1
Ukiah Valley Sanitation District | [6 empty] | 19356 |  | 1613 | 19356 | 0% | 0% | 0% | [6 empty] | 1
UKIAH, CITY OF | 100-150 | 100-150 |  |  | 75.5 | 75.5 | 19356 |  | 1613 | 19356 | 0% | 0% | 4.681% |  |  | 1 |  |  |  | 1
Ukiah City WWTP | [8 empty] | 1613 | 19356 | 0% | 0% | 0% | [6 empty] | 1
Upper Russian River Water Agency | [6 empty] | 36346 |  | 3028.8333 | 36346 | 0% | 0% | 0% | [6 empty] | 1
VALLEY FORD WATER ASSOCIATION |  | over $100 |  |  |  |  | 46319 |  | 3859.9167 | 46319 | 0% | 0% | 0% | [6 empty] | 1
VINEHILL VISTA MUTUAL WATER COMPANY | [6 empty] | 63859 |  | 5321.5833 | 63859 | 0% | 0% | 0% | [6 empty] | 1
WADDINGTON W.W. | [6 empty] | 38750 |  | 3229.1667 | 38750 | 0% | 0% | 0% | [6 empty] | 1
WAYSIDE GARDENS MOBILE HOME PARK | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
WEAVERVILLE C.S.D. | 0-50 | 0-50 | 25 |  |  | 25 | 40455 |  | 3371.25 | 40455 | 0.7416% | 0% | 0% | [6 empty] | 1
WEAVERVILLE S.D. |  | $0-50 |  |  |  |  | 40455 |  | 3371.25 | 40455 | 0% | 0% | 0% | [6 empty] | 1
WEED, CITY OF | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 18125 |  | 1510.4167 | 18125 | 0% | 0% | 4.999% |  |  | 1 |  |  |  | 1
WEOTT C.S.D. | 100-150; If there are no water usage overages, the average bill for combined water and wastewater is roughly $104. | 100-150; If there are no water usage overages, the average bill for combined water and wastewater is roughly $104. |  |  | 104 | 104 | 33438 |  | 2786.5 | 33438 | 0% | 0% | 3.732% | [6 empty] | 1
WENDELL WATER COMPANY (PUC) | [6 empty] | 52396 |  | 4366.3333 | 52396 | 0% | 0% | 0% | [6 empty] | 1
WEST PARK PROPERTIES | [6 empty] | 26544 |  | 2212 | 26544 | 0% | 0% | 0% | [6 empty] | 1
WEST WATER COMPANY (PUC) | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 37411 |  | 3117.5833 | 37411 | 2.422% | 0% | 0% | [6 empty] | 1
WESTERN MOBILE HOME PARK | [6 empty] | 29250 |  | 2437.5 | 29250 | 0% | 0% | 0% | [6 empty] | 1
WESTHAVEN C.S.D. | 51-100; water only | 51-100; water only | 75.5 |  |  | 75.5 | 50417 |  | 4201.4167 | 50417 | 1.797% | 0% | 0% | [6 empty] | 1
WESTPORT COUNTY WATER DISTRICT | The basic rate for water and sewer is $83.01 per month for each residential and commercial user. lthough the District has meters on each service, basic residential rates are based on a usage of 12,000 gallons per month. Water use in excess of 12,000 gallons per month is charged according to amount of usage. | The basic rate for water and sewer is $83.01 per month for each residential and commercial user. lthough the District has meters on each service, basic residential rates are based on a usage of 12,000 gallons per month. Water use in excess of 12,000 gallons per month is charged according to amount of usage. |  |  | 83.01 | 83.01 | 55370 |  | 4614.1667 | 55370 | 0% | 0% | 1.799% | [6 empty] | 1
Wildwood Campground | [6 empty] | 48563 |  | 4046.9167 | 48563 | 0% | 0% | 0% | [6 empty] | 1
WILDWOOD RETREAT (WILDWOOD CONSERVATION FOUNDATION) | [6 empty] | 45489 |  | 3790.75 | 45489 | 0% | 0% | 0% | [6 empty] | 1
Willits City WWTP | [6 empty] | 32667 |  | 2722.25 | 32667 | 0% | 0% | 0% | [6 empty] | 1
WILLITS, CITY OF | 51-100 | 51-100 |  |  | 75.5 | 75.5 | 32667 |  | 2722.25 | 32667 | 0% | 0% | 2.773% | [6 empty] | 1
WILLOW COUNTY WATER DISTRICT | 51-100 | 51-100 | 75.5 |  |  | 75.5 | 19356 |  | 1613 | 19356 | 4.681% | 0% | 0% | 1 | [5 empty] | 1
WILLOW CREEK C.S.D. | 0-50; we have high bills in the summer when persons are using lots of water for irrigation of lawns, gardens and cannabis. | 0-50; we have high bills in the summer when persons are using lots of water for irrigation of lawns, gardens and cannabis. | 25 |  |  | 25 | 32209 |  | 2684.0833 | 32209 | 0.9314% | 0% | 0% | [6 empty] | 1
WILLOWSIDE MUTUAL WATER COMPANY | [6 empty] | 42958 |  | 3579.8333 | 42958 | 0% | 0% | 0% | [6 empty] | 1
WILSHIRE HEIGHTS MUTUAL WATER COMPANY | [6 empty] | 46037 |  | 3836.4167 | 46037 | 0% | 0% | 0% | [6 empty] | 1
WINDSOR, TOWN OF | [6 empty] | 39614 |  | 3301.1667 | 39614 | 0% | 0% | 0% | [6 empty] | 1
Woods, The (Mendocino) | 57 | 57 |  |  | 57 | 57 | 39667 |  | 3305.5833 | 39667 | 0% | 0% | 1.724% | [6 empty] | 1
WOODSIDE RV PARK & CAMPGROUND | Water and Sewer are included as part of the Monthly Rental rate Per Space. There is currently no breakdowns for what portion of the Monthly rate is for those utilities. | Water and Sewer are included as part of the Monthly Rental rate Per Space. There is currently no breakdowns for what portion of the Monthly rate is for those utilities. |  |  |  |  | 31027 |  | 2585.5833 | 31027 | 0% | 0% | 0% | [6 empty] | 1
YREKA, CITY OF | 0-50; ~$48 for water alone | 0-50; ~$48 for water alone | 48 |  |  | 48 | 25493 |  | 2124.4167 | 25493 | 2.259% | 0% | 0% | [6 empty] | 1
YULUPA MUTUAL WATER COMPANY | 100-150 | 100-150 | 125 |  |  | 125 | 46037 |  | 3836.4167 | 46037 | 3.258% | 0% | 0% | 1 | [5 empty] | 1
[11 empty] | Totals |  |  | 17 | 6 | 6 | 3 | 3 | 6 | 308
* Stratus Consulting. 2013. Affordability Assessment Tool for Federal Water Mandates. Prepared for US Conference of Mayors, American Water Works Association, and Water Environment Federation. https://www.awwa.org/Portals/0/AWWA/ETS/Resources/AffordabilityAssessmentTool.pdf
** Corona Environmental Consulting et al. 2019. Developing a New Framework for Household Affordability and Financial Capability Assessment in the Water Sector. https://www.awwa.org/Portals/0/AWWA/ETS/Resources/DevelopingNewFrameworkForAffordability.pdf?ver=2020-02-03-090519-813
[14 empty] | 4.928% | 1.739% | 1.739% | 0.8696% | 0.8696% | 1.739%
[17 empty] | lowfinancial impact | mid-range fiancial impact | high financial impact

## Sheet1 (hidden)
technical |  | sewer
managerial | groundwater | septic
financial | surface water
trainings | both
staffing | other
other

## DAC, SDAC, EDA calculations
[7 empty] | % Monthly MHI |  |  | EPA Affordability Criteria Threshold * |  |  |  | System Financial Capability Assmnt
Water/ Wastewater System | Median Household Income (MHI) | DAC | SDAC | EDA | Advantaged | MHI known | Water | Wastewater | Both | Water > 2.5% | WW > 2% | Both > 4.5% |  | RI - WW bill as % MHI*, ** |  | Systems that trigger affordability criteria and are:
|  | $38,270<MHI< $51,026 | MHI< $38,270 | $51,026<MHI< $54,216 | [8 empty] | < 1% | 1 - 2% | > 2% | & DAC | & SDAC | & EDA | Advantaged
AIRPORT/LARKFIELD/WIKIUP SANITATION ZONE (ALWSZ) | 46037 | 1 |  |  |  | 1
ALBION MUTUAL WATER COMPANY | 39667 | 1 |  |  |  | 1 | 1.528%
ALDERPOINT COUNTY WATER | 26813 |  | 1 |  |  | 1 | 1.79%
ALEXANDER VALLEY ACRES WATER COMPANY | 57639 |  |  |  | 1 | 1
ANCIENT REDWOODS R.V. PARK PWS #120 6011 | 48542 | 1 |  |  |  | 1
Anderson Valley Community Services District | 36932 |  | 1 |  |  | 1
ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | 45489 | 1 |  |  |  | 1
ATHENA TERRACE MUTUAL WATER COMPANY | 46037 | 1 |  |  |  | 1
AUSTIN ACRES MUTUAL WATER COMPANY | 58333 |  |  |  | 1 | 1
Austin Creek Mutual (Springhill) | 41389 | 1 |  |  |  | 1
AZALEA GLEN | 50417 | 1 |  |  |  | 1
BAR 717 RANCH, INC. (SUMMER CAMP) | 50417 | 1 |  |  |  | 1
BEACH CREEK MH PARK | 20346 |  | 1 |  |  | 1
BELMONT TERRACE MUTUAL WATER COMPANY | 99141 |  |  |  | 1 | 1
BENBOW W.C. | 36371 |  | 1 |  |  | 1
BENNETT RIDGE MUTUAL WATER COMPANY | 46037 | 1 |  |  |  | 1
BERTSCH OCEANVIEW CSD | 26544 |  | 1 |  |  | 1 | 0.9968%
BIG LAGOON CSD | 50417 | 1 |  |  |  | 1 | 1.797%
BIG LAGOON PARK WATER CO. | 20346 |  | 1 |  |  | 1 | 1.474%
BIG RIVER VISTA MUTUAL WATER COMPANY | 51277 |  |  | 1 |  | 1 | 2.118%
BIG ROCK C.S.D. | 26544 |  | 1 |  |  | 1 | 3.413% |  |  | 1 | [6 empty] | 1
BLUE LAKE, CITY OF | 49828 | 1 |  |  |  | 1 |  |  | 1.818%
BLUE SPRUCE MOBILE HOME PARK | 64612 |  |  |  | 1 | 1
BODEGA BAY PUBLIC UTILITY DISTRICT | 85526 |  |  |  | 1 | 1
BODEGA WATER COMPANY | 85526 |  |  |  | 1 | 1
BRAND WATER COMPANY | 46037 | 1 |  |  |  | 1
BRANGER MUTUAL WATER COMPANY, INC. | 46037 | 1 |  |  |  | 1
Branscomb Mutual Water Company | 32667 |  | 1 |  |  | 1
BRICELAND C.S.D. | 37778 |  | 1 |  |  | 1 | 0.7941%
BROOKTRAILS TOWNSHIP CSD | 32667 |  | 1 |  |  | 1
BROOKWOOD MOBILE HOME PARK | 46037 | 1 |  |  |  | 1
BUCHER WATER COMPANY | 57639 |  |  |  | 1 | 1
BUCKTAIL MUTUAL WATER COMPANY | 30000 |  | 1 |  |  | 1 | 0.1022%
BUD FINE MWC | 30000 |  | 1 |  |  | 1
BURNT RANCH ESTATES Mutual Water Co. | 39167 | 1 |  |  |  | 1 | 0.766%
BUTTE MOBILE HOME PARK | 26544 |  | 1 |  |  | 1 | 1.13%
CAL ORE MOBILE ESTATES | 34000 |  | 1 |  |  | 1
California American GEYSERVILLE WATER WORKS (PUC) | 46250 | 1 |  |  |  | 1
Green Diamond Resource Company - Korbel | 38816 | 1 |  |  |  | 1
CALIFORNIA-AMERICAN WATER LARKFIELD (PUC) | 46037 | 1 |  |  |  | 1
CALLAHAN WATER DISTRICT | 44242 | 1 |  |  |  | 1 | 0.6781%
CALPELLA COUNTY WATER DISTRICT | 19356 |  | 1 |  |  | 1 |  |  | 7.75% |  |  | 1 |  |  |  |  | 1
CAMP LIAHONA REDWOODS (YOUTH SUMMER CAMP) | 39614 | 1 |  |  |  | 1
CAMP MEEKER WATER SYSTEM | 70714 |  |  |  | 1 | 1
CAMP ROYANEH | 49886 | 1 |  |  |  | 1
CANON MANOR WATER SYSTEM | 46037 | 1 |  |  |  | 1
CASPAR SOUTH SERVICE COMPANY | 46037 | 1 |  |  |  | 1 | 3.258% |  |  | 1 | [5 empty] | 1
Caspar South Water District | 46037 | 1 |  |  |  | 1
CAZADERO WATER COMPANY, INC. | 49886 | 1 |  |  |  | 1 | 0.6014%
CHINOOK WATER SYSTEM | 27200 |  | 1 |  |  | 1
Church Tree CSD | 26544 |  | 1 |  |  | 1
CITY OF ARCATA | 28277 |  | 1 |  |  | 1 |  |  | 3.204%
CITY OF COTATI | 50667 | 1 |  |  |  | 1
CITY OF ETNA | 30089 |  | 1 |  |  | 1
City of Ferndale | 38750 | 1 |  |  |  | 1
City of Fortuna WWTP | 49403 | 1 |  |  |  | 1
CITY OF FORTUNA | 49403 | 1 |  |  |  | 1 |  |  | 3.036%
CITY OF ROHNERT PARK | 71576 |  |  |  | 1 | 1 |  |  | 2.096%
CITY OF SANTA ROSA | 46037 | 1 |  |  |  | 1 |  |  | 3.258%
CLEAR CREEK WATER COMPANY | 63229 |  |  |  | 1 | 1
CLOVERDALE, CITY OF | 63229 |  |  |  | 1 | 1 |  |  | 2.372%
COLONIAL PARK | 57639 |  |  |  | 1 | 1
COPCO LAKE MWC | 40938 | 1 |  |  |  | 1
COVE MOBILE VILLA | 25493 |  | 1 |  |  | 1
COVELO C.S.D. | 29167 |  | 1 |  |  | 1 |  |  | 3.106%
COVELO MOBILE HOME PARK | 29167 |  | 1 |  |  | 1
COVINGTON MILL MWC-DIVISION B | 32321 |  | 1 |  |  | 1 | 0.9282%
Creekside Cabins & RV Resort | 45299 | 1 |  |  |  | 1
CRESCENT CITY, CITY OF | 26544 |  | 1 |  |  | 1 |  |  | 3.413%
CRIVELLI'S WATER SYSTEM | 27200 |  | 1 |  |  | 1
DEL NORTE COUNTY COMMUNITY SERVICE AREA | 26544 |  | 1 |  |  | 1 | 0.2939%
DELORES LANE WATER SYSTEM | 46037 | 1 |  |  |  | 1
Dolphin Isle Marina | 31027 |  | 1 |  |  | 1
DORRIS, CITY OF | 31923 |  | 1 |  |  | 1 | 1.569% | 0.686% |  |  |  |  | 1 |  |  |  | 1
Dos Rios Mutual Water Company | 23315 |  | 1 |  |  | 1
DOWNTOWN GRATON MUTUAL WATER SYSTEM | 99141 |  |  |  | 1 | 1
EAST AUSTIN CREEK MUTUAL WATER COMPANY | 49886 | 1 |  |  |  | 1
EL CRYSTAL MOBILE HOME PARK | 46037 | 1 |  |  |  | 1
EL PORTAL MOBILE ESTATES | 29250 |  | 1 |  |  | 1
ELK COUNTY WATER DISTRICT | 39667 | 1 |  |  |  | 1
EMERALD FOREST | 50417 | 1 |  |  |  | 1
END-O-VALLEY MUTUAL WATER COMPANY | 46037 | 1 |  |  |  | 1 | 1.955%
EUREKA, CITY OF, ELK RIVER WWTP | 20346 |  | 1 |  |  | 1
EUREKA, CITY OF | 20346 |  | 1 |  |  | 1
FARMER WATER SYSTEM | 99141 |  |  |  | 1 | 1
FERNDALE - DEL ORO WATER CO. | 38750 | 1 |  |  |  | 1 |  | 2.044% |  |  | 1 |  |  |  | 1 | 1
FIELDBROOK GLENDALE C.S.D. | 20346 |  | 1 |  |  | 1 | 2.654% | 4.482% |  | 1 | 1 |  |  |  | 1 |  | 1
FIRCREST MUTUAL WATER COMPANY | 99141 |  |  |  | 1 | 1
Forestville Water District | 38792 | 1 |  |  |  | 1
FORT BRAGG MUNICIPAL IMP DISTRCT | 31027 |  | 1 |  |  | 1
Fort Bragg City WWTP | 31027 |  | 1 |  |  | 1
FORT BRAGG, CITY OF | 31027 |  | 1 |  |  | 1 |  |  | 4.834% |  |  | 1 |  |  |  |  | 1
FORT JONES, TOWN OF | 45365 | 1 |  |  |  | 1 |  |  | 1.323%
GARBERVILLE SANITARY DISTRICT | 36371 |  | 1 |  |  | 1
GASQUET C.S.D. | 35769 |  | 1 |  |  | 1 | 0.8387%
GEYSERVILLE SANITATION ZONE | 46250 | 1 |  |  |  | 1
GILL CREEK MUTUAL WATER COMPANY | 46250 | 1 |  |  |  | 1
GOLDEN BEAR RV PARK | 27200 |  | 1 |  |  | 1
Graton CSD | 74355 |  |  |  | 1 | 1
GRATON MUTUAL (GREEN VALLEY HOA) | 71576 |  |  |  | 1 | 1
GREEN ACRES TRAILER PARK | 31027 |  | 1 |  |  | 1
GRENADA SANITARY DISTRICT | 43523 | 1 |  |  |  | 1 |  |  | 2.082%
Gualala Community Services District | 40185 | 1 |  |  |  | 1
HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM | 71576 |  |  |  | 1 | 1
HAPPY CAMP C.S.D. | 41000 | 1 |  |  |  | 1
HAPPY CAMP S.D. | 41000 | 1 |  |  |  | 1
HAWKINS WATER CO-CAL WATER SERVICE (PUC) | 61576 |  |  |  | 1 | 1
HEALDSBURG, CITY OF | 57639 |  |  |  | 1 | 1
HEIGHTS MUTUAL WATER COMPANY | 42958 | 1 |  |  |  | 1
HERITAGE HOUSE RESORT AND SURFWOOD MUTUAL WATER CORP. | 31027 |  | 1 |  |  | 1
HILLS RANCH MUTUAL WATER COMPANY | 39667 | 1 |  |  |  | 1 | 2.738% |  |  | 1 | [5 empty] | 1
HILTON MUTUAL WATER COMPANY | 49732 | 1 |  |  |  | 1
HOLLAND HEIGHTS MUTUAL WATER COMPANY | 46037 | 1 |  |  |  | 1
HOLLY RANCH VILLAGE | 39667 | 1 |  |  |  | 1
HOPLAND PUBLIC UTILITY DISTRICT | 19356 |  | 1 |  |  | 1 |  |  | 7.75% |  |  | 1 |  |  |  |  | 1
HORNBROOK C.S.D. | 33000 |  | 1 |  |  | 1
Hussey Ranch Corporation (HRC) C.S.D. | 26544 |  | 1 |  |  | 1
HUCKLEBERRY MUTUAL WATER COMPANY | 35000 |  | 1 |  |  | 1 | 2.589% |  |  | 1 | [6 empty] | 1
HUMBOLDT BAY MWD | 20346 |  | 1 |  |  | 1 | 1.474%
HUMBOLDT C.S.D. | 44257 | 1 |  |  |  | 1 |  |  | 2.047%
Humboldt County RID #1, Shelter Cove POTW | 42118 | 1 |  |  |  | 1
HUNTER VALLEY CSD | 27200 |  | 1 |  |  | 1 | 0.7059%
HYDESVILLE CO. W.D. | 56042 |  |  |  | 1 | 1
INDIAN CREEK TRAILER PARK | 50313 | 1 |  |  |  | 1 | 0.5963%
IRISH BEACH WATER DISTRICT | 48828 | 1 |  |  |  | 1
JACOBY CREEK CSD - combined with City of Arcata | 28277 |  | 1 |  |  | 1
JED SMITH HOMEOWNERS ASSN. | 26544 |  | 1 |  |  | 1 | 3.413% |  |  | 1 | [6 empty] | 1
JUNIPER CREEK ESTATES | 45365 | 1 |  |  |  | 1
KAMP KLAMATH CORP. | 27200 |  | 1 |  |  | 1
KELLY MUTUAL WATER COMPANY | 99141 |  |  |  | 1 | 1
KLAMATH C.S.D. (Del Norte Community Development) | 27200 |  | 1 |  |  | 1 | 1.588% | 0.8118% |  |  |  |  | 1 |  |  |  | 1
KLAMATH CAMPER CORRAL | 27200 |  | 1 |  |  | 1
KLAMATH RIVER RV PARK | 27200 |  | 1 |  |  | 1
LAKE SHASTINA C.S.D | 18125 |  | 1 |  |  | 1 |  |  | 4.999% |  |  | 1 |  |  |  |  | 1
LAKE VIEW MUTUAL WATER CO. | 60692 |  |  |  | 1 | 1
LAS PALMAS MOBILE HOME PARK | 69732 |  |  |  | 1 | 1
LAYTONVILLE COUNTY WATER DISTRICT | 23315 |  | 1 |  |  | 1 | 3.886% |  |  | 1 | [6 empty] | 1
LEISURE MOBILE HOME PARK | 54497 |  |  |  | 1 | 1
LEWISTON Community Services District | 30000 |  | 1 |  |  | 1 | 1.84% | 2.16% |  |  | 1 |  |  |  | 1 |  | 1
LITTLE LAKE MOBILE HOME PARK | 32667 |  | 1 |  |  | 1
LOLETA C.S.D. | 46458 | 1 |  |  |  | 1
LONE PINE MUTUAL WATER COMPANY | 99141 |  |  |  | 1 | 1
MACDOEL WATERWORKS | 28500 |  | 1 |  |  | 1
MADRONA MANOR 140330 | 57639 |  |  |  | 1 | 1
MADRONE MUTUAL WATER COMPANY | 50667 | 1 |  |  |  | 1
MAGIC MOUNTAIN MUTUAL WATER COMPANY | 37308 |  | 1 |  |  | 1 |  |  | 2.412%
MANILA COMMUNITY SERVICES DIST. | 38816 | 1 |  |  |  | 1
MCCLOUD C.S.D. | 39083 | 1 |  |  |  | 1
MARK WEST ACRES MWC | 46037 | 1 |  |  |  | 1
MARK WEST MUTUAL WATER CO. | 46037 | 1 |  |  |  | 1
MCKINLEYVILLE C.S.D. | 46708 | 1 |  |  |  | 1 |  |  | 3.211%
MEADOW ESTATES MUTUAL | 36932 |  | 1 |  |  | 1 | 2.453%
MELITA HEIGHTS MUTUAL WATER COMPANY | 46037 | 1 |  |  |  | 1
MENDOCINO CITY C.S.D. | 51277 |  |  | 1 |  | 1 |  |  | 1.767%
MENDOCINO COUNTY WATER WORKS DISTRICT NO. II | 40185 | 1 |  |  |  | 1
MICHELE MUTUAL WATER COMPANY | 42958 | 1 |  |  |  | 1
MILL CREEK M.W.C. | 49403 | 1 |  |  |  | 1
MILLVIEW COUNTY WATER DISTRICT | 19356 |  | 1 |  |  | 1
MIRANDA C.S.D. | 33438 |  | 1 |  |  | 1 | 0.4306% | 0.8254% |  |  |  |  | 1 |  |  |  | 1
MOBILE HOME ESTATES | 46037 | 1 |  |  |  | 1 | 0.6516%
MONTAGUE, CITY OF | 40938 | 1 |  |  |  | 1
MONTAGUE WATER CONSERVATION DISTRICT | 40938 | 1 |  |  |  | 1
Montair Subdivision Homeowners Association | 54844 |  |  |  | 1 | 1 |  | 1.094% | [5 empty] | 1 |  |  |  |  | 1
MOONSTONE HEIGHTS MWA | 50417 | 1 |  |  |  | 1
MOUNT WESKE ESTATES MUTUAL WATER COMPANY | 39614 | 1 |  |  |  | 1
MOUNTAIN VIEW MOBILE ESTATES, LLC | 44604 | 1 |  |  |  | 1
MYERS FLAT M.W.S. INC. | 33438 |  | 1 |  |  | 1 | 2.62% |  |  | 1 | [6 empty] | 1
NEVES FAMILY TRUST WATER SYSTEM | 90179 |  |  |  | 1 | 1
NEWELL COUNTY WATER DISTRICT | 33909 |  | 1 |  |  | 1
NOEL HEIGHTS-CAL WATER SERVICE (PUC) | 40469 | 1 |  |  |  | 1
NORTH GUALALA WATER COMPANY | 40185 | 1 |  |  |  | 1 | 2.255%
NORTH STAR MOBILE HOME PARK | 46037 | 1 |  |  |  | 1
NOYO HARBOR DISTRICT | 31027 |  | 1 |  |  | 1
OAK VALLEY ACRES P.O.A. | 25493 |  | 1 |  |  | 1
OCCIDENTAL COMMUNITY SERVICES DISTRICT | 69219 |  |  |  | 1 | 1
OCCIDENTAL COUNTY SANITATION DISTRICT | 69219 |  |  |  | 1 | 1
Odd Fellows Recreation Club | 40469 | 1 |  |  |  | 1
ORICK C.S.D. | 47621 | 1 |  |  |  | 1
ORLEANS C.S.D. | 40129 | 1 |  |  |  | 1 | 0.7476%
ORLEANS MUTUAL WATER CO. | 40129 | 1 |  |  |  | 1
PACIFIC REEFS WATER DISTRICT | 39667 | 1 |  |  |  | 1
PALMER CREEK CSD | 49403 | 1 |  |  |  | 1
PALOMINO ESTATES M.W.C. | 36371 |  | 1 |  |  | 1 | 4.124% |  |  | 1 | [6 empty] | 1
PALOMINO LAKES MUTUAL WATER CO. | 37411 |  | 1 |  |  | 1
PARK ROYAL MUTUAL WATER | 46037 | 1 |  |  |  | 1
PATRICK CREEK COMMUNITY SERVICE DISTRICT | 46708 | 1 |  |  |  | 1
PHILLIPSVILLE C.S.D. | 33438 |  | 1 |  |  | 1
Pine Cove RV Park | 39583 | 1 |  |  |  | 1
PINE GROVE Mobile Home PARK | 26544 |  | 1 |  |  | 1
PINE HILL TERRACE MOBILE HOME PARK | 99141 |  |  |  | 1 | 1
PINE MOUNTAIN MUTUAL WATER CO. | 32667 |  | 1 |  |  | 1 | 2.59% |  |  | 1 | [6 empty] | 1
PLAZA MOBILE HOME PARK | 29250 |  | 1 |  |  | 1
POINT ARENA WATER WORKS | 40208 | 1 |  |  |  | 1
Point Arena WWTP | 40208 | 1 |  |  |  | 1
Point Arena Lighthouse Keepers | 40208 | 1 |  |  |  | 1
POINT CABRILLO HIGHLANDS | 56250 |  |  |  | 1 | 1
POINT OF VIEW MUTUAL WATER CO | 51277 |  |  | 1 |  | 1 | 1.767%
RAINS CREEK WATER DISTRICT | 49732 | 1 |  |  |  | 1
RANCHO DEL PARADISO-CAL WATER SVC (PUC) | 58333 |  |  |  | 1 | 1
RANDAL'S RANCHETTE MUTUAL WATER CO. | 46037 | 1 |  |  |  | 1
REDCREST WATER WORKS | 48542 | 1 |  |  |  | 1
REDWAY C.S.D. | 37778 |  | 1 |  |  | 1
REDWOOD HEIGHTS WATER ASSOCIATION | 49886 | 1 |  |  |  | 1
REDWOOD PARK C.S.D. | 27200 |  | 1 |  |  | 1 |  |  | 1.103%
REDWOOD VALLEY COUNTY WATER DISTRICT | 60692 |  |  |  | 1 | 1 | 0.4943%
Reservation Ranch | 42944 | 1 |  |  |  | 1
RESORT IMPRVMT. DIST. #1 | 41140 | 1 |  |  |  | 1 |  |  | 3.646%
White Deer Lodge Water System (formerly Ridge Water System) | 32667 |  | 1 |  |  | 1
RIDGEWOOD WATER SYSTEM | 32667 |  | 1 |  |  | 1
RIEBLI MUTUAL WATER COMPANY | 42958 | 1 |  |  |  | 1
RINCON VALLEY MOBILE ESTATES | 44390 | 1 |  |  |  | 1
RIO DELL, CITY OF | 47639 | 1 |  |  |  | 1 | 1.557% | 1.798% | [5 empty] | 1 |  | 1
(Russian) RIVER ESTATES MUTUAL WATER COMPANY | 19356 |  | 1 |  |  | 1
Riverbend Mobile Home Park | 28277 |  | 1 |  |  | 1
RIVERSIDE CSD | 52679 |  |  | 1 |  | 1
ROGINA WATER COMPANY INC. | 73523 |  |  |  | 1 | 1
ROLLING OAKS ROAD ASSOCIATION | 49726 | 1 |  |  |  | 1
ROSELAND MOBILE HOME PARK | 46037 | 1 |  |  |  | 1
RUSH CREEK MUTUAL WATER SYSTEM | 40455 | 1 |  |  |  | 1 | 0.7416%
RUSSIAN RIVER COUNTY SANITATION DISTRICT | 46037 | 1 |  |  |  | 1 |  | 3.232% |  |  | 1 |  |  |  | 1 | 1
RUSSIAN RIVER MUTUAL WATER CO. | 57639 |  |  |  | 1 | 1
RUTH LAKE MARINA AND RECREATION AREA | 25395 |  | 1 |  |  | 1
SALYER HEIGHTS W.S., INC | 35104 |  | 1 |  |  | 1
SALYER MUTUAL WC (FORMERLY RIVERVIEW AC) | 35104 |  | 1 |  |  | 1
SANTA ROSA MOBILE ESTATES | 49306 | 1 |  |  |  | 1
SAWYERS BAR COUNTY WATER DISTRICT | 32500 |  | 1 |  |  | 1 | 5.575% |  |  | 1 | [6 empty] | 1
Scotia CSD | 48542 | 1 |  |  |  | 1
SEA RANCH SANITATION ZONE | 62750 |  |  |  | 1 | 1
SEA RANCH WATER COMPANY,THE (PUC) | 62750 |  |  |  | 1 | 1
SEAFAIR ROAD AND WATER COMPANY | 51277 |  |  | 1 |  | 1 | 2.925% |  |  | 1 | [7 empty] | 1
SEAWOOD ESTATES MUTUAL WATER | 50417 | 1 |  |  |  | 1
SEBASTOPOL, CITY OF | 99141 |  |  |  | 1 | 1 |  |  | 1.513%
SEQUOIA WATER COMPANY | 52396 |  |  | 1 |  | 1
SERENO DEL MAR WATER CO. | 49732 | 1 |  |  |  | 1
SEYMOUR'S MUTUAL WATER SYSTEM | 32321 |  | 1 |  |  | 1 | 0.9282%
SHADOW MOUNTAIN MHP | 46037 | 1 |  |  |  | 1
SHAMROCK MOBILE HOME PARK | 46037 | 1 |  |  |  | 1
SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | 25493 |  | 1 |  |  | 1 | 3.248% |  |  | 1 | [6 empty] | 1
SHASTINA MOBILE ESTATES | 18125 |  | 1 |  |  | 1
SHORELANDS ROAD & WATER COMPANY | 51277 |  |  | 1 |  | 1 | 1.767%
SISKIYOU CO. ROLLING HILLS MWC | 25493 |  | 1 |  |  | 1
SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system) | 18125 |  | 1 |  |  | 1
Six Acres Water Company | 37411 |  | 1 |  |  | 1
SMITH RIVER C.S.D. | 42944 | 1 |  |  |  | 1
SONOMA COUNTY CSA 41-FITCH MOUNTAIN | 46037 | 1 |  |  |  | 1
SONOMA COUNTY CSA 41-FREESTONE | 46037 | 1 |  |  |  | 1
SONOMA COUNTY CSA 41-JENNER | 46037 | 1 |  |  |  | 1
SONOMA COUNTY CSA 41-SALMON CREEK | 46037 | 1 |  |  |  | 1 |  | 2.607% |  |  | 1 |  |  |  | 1 | 1
SONOMA COUNTY MUTUAL WATER COMPANY | 41389 | 1 |  |  |  | 1 | 0.7248%
SONOMA COUNTY WATER AGENCY | 46037 | 1 |  |  |  | 1
SONOMA MOUNTAIN COUNTY WATER DISTRICT | 46037 | 1 |  |  |  | 1
SONOMA WEST HOLDINGS NORTH PLANT | 99141 |  |  |  | 1 | 1
SOUNDS OF THE SEAS W. S. | 50417 | 1 |  |  |  | 1
SOUTH CLOVERDALE WATER COMPANY | 37411 |  | 1 |  |  | 1 | 2.422%
SOUTH PARK COUNTY SANITATION DISTRICT | 46037 | 1 |  |  |  | 1
STEWARTS POINT WATER SYSTEM | 61786 |  |  |  | 1 | 1
STONEGATE MOBILE HOME PARK | 65516 |  |  |  | 1 | 1
SUMMIT VIEW RANCH MUTUAL WATER CO. | 46037 | 1 |  |  |  | 1
SUNRISE MOUNTAIN MUTUAL WATER COMPANY | 41389 | 1 |  |  |  | 1
SUNSET PARK COMMUNITY | 46037 | 1 |  |  |  | 1 | 0.6516%
SURFWOOD MUTUAL WATER CORPORATION | 51277 |  |  | 1 |  | 1 | 1.767%
SWEETWATER SPRINGS CWD - GUERNEVILLE | 45489 | 1 |  |  |  | 1 | 1.992%
SWEETWATER SPRINGS CWD - MONTE RIO | 45489 | 1 |  |  |  | 1 | 1.992%
SYLVAN HARBOR TRAILER PARK | 50417 | 1 |  |  |  | 1
TENNANT C.S.D. | 31923 |  | 1 |  |  | 1 |  |  | 0.9398%
TERRACE VIEW WATER SYSTEM | 49726 | 1 |  |  |  | 1
TIMBER COVE COUNTY WATER DISTRICT | 41389 | 1 |  |  |  | 1
TREASURE CREEK WOODS MWC | 32321 |  | 1 |  |  | 1 | 1.392%
Trinidad Extended Stay | 50417 | 1 |  |  |  | 1
TRINIDAD, CITY OF | 50417 | 1 |  |  |  | 1
TRINITY CENTER M.W.C. . | 32321 |  | 1 |  |  | 1
TRINITY CO. W.W. DIST #1 | 28553 |  | 1 |  |  | 1 | 1.229% | 1.051% | [5 empty] | 1 |  |  | 1
TRINITY KNOLLS MUTUAL WATER COMPANY | 32321 |  | 1 |  |  | 1 | 2.803% |  |  | 1 | [6 empty] | 1
TRINITY VILLAGE MUTUAL WATER CO. | 35104 |  | 1 |  |  | 1
TRIUMPH LIFE CAMP (TLC) YOUTH SUMMER CAMP | 35000 |  | 1 |  |  | 1
TULELAKE, CITY OF | 33909 |  | 1 |  |  | 1 |  | 2.672% |  |  | 1 |  |  |  | 1 |  | 1
TWIN HILLS MUTUAL WATER COMPANY | 52396 |  |  | 1 |  | 1
Ukiah Valley Sanitation District | 19356 |  | 1 |  |  | 1
UKIAH, CITY OF | 19356 |  | 1 |  |  | 1 |  |  | 4.681% |  |  | 1 |  |  |  |  | 1
Ukiah City WWTP | 19356 |  | 1 |  |  | 1
Upper Russian River Water Agency | 36346 |  | 1 |  |  | 1
VALLEY FORD WATER ASSOCIATION | 46319 | 1 |  |  |  | 1
VINEHILL VISTA MUTUAL WATER COMPANY | 63859 |  |  |  | 1 | 1
WADDINGTON W.W. | 38750 | 1 |  |  |  | 1
WAYSIDE GARDENS MOBILE HOME PARK | 46037 | 1 |  |  |  | 1
WEAVERVILLE C.S.D. | 40455 | 1 |  |  |  | 1 | 0.7416%
WEAVERVILLE S.D. | 40455 | 1 |  |  |  | 1
WEED, CITY OF | 18125 |  | 1 |  |  | 1 |  |  | 4.999% |  |  | 1 |  |  |  |  | 1
WEOTT C.S.D. | 33438 |  | 1 |  |  | 1 |  |  | 3.732%
WENDELL WATER COMPANY (PUC) | 52396 |  |  | 1 |  | 1
WEST PARK PROPERTIES | 26544 |  | 1 |  |  | 1
WEST WATER COMPANY (PUC) | 37411 |  | 1 |  |  | 1 | 2.422%
WESTERN MOBILE HOME PARK | 29250 |  | 1 |  |  | 1
WESTHAVEN C.S.D. | 50417 | 1 |  |  |  | 1 | 1.797%
WESTPORT COUNTY WATER DISTRICT | 55370 |  |  |  | 1 | 1 |  |  | 1.799%
Wildwood Campground | 48563 | 1 |  |  |  | 1
WILDWOOD RETREAT (WILDWOOD CONSERVATION FOUNDATION) | 45489 | 1 |  |  |  | 1
Willits City WWTP | 32667 |  | 1 |  |  | 1
WILLITS, CITY OF | 32667 |  | 1 |  |  | 1 |  |  | 2.773%
WILLOW COUNTY WATER DISTRICT | 19356 |  | 1 |  |  | 1 | 4.681% |  |  | 1 | [6 empty] | 1
WILLOW CREEK C.S.D. | 32209 |  | 1 |  |  | 1 | 0.9314%
WILLOWSIDE MUTUAL WATER COMPANY | 42958 | 1 |  |  |  | 1
WILSHIRE HEIGHTS MUTUAL WATER COMPANY | 46037 | 1 |  |  |  | 1
WINDSOR, TOWN OF | 39614 | 1 |  |  |  | 1
Woods, The (Mendocino) | 39667 | 1 |  |  |  | 1 |  |  | 1.724%
WOODSIDE RV PARK & CAMPGROUND | 31027 |  | 1 |  |  | 1
YREKA, CITY OF | 25493 |  | 1 |  |  | 1 | 2.259%
YULUPA MUTUAL WATER COMPANY | 46037 | 1 |  |  |  | 1 | 3.258% |  |  | 1 | [5 empty] | 1
Total Systems | 308 | 141 | 112 | 10 | 45 | 308 | Totals |  |  | 16 | 6 | 7 | 3 | 3 | 6 | 7 | 24 | 1 | 1 | 33
Percentages of total number of systems |  | 45.78% | 36.36% | 3.247% | 14.61% | 100% |  |  |  | 5.195% | 1.948% | 2.273% | 0.974% | 0.974% | 1.948% | 21.21% | 72.73% | 3.03% | 3.03%
|  |  | 263 | 0.8539
MHI: 18 to start unknown MHI: looked up physical address and used existing table data as MHI.

## H2O System Classification
Water/ Wastewater System | Federal Type | Why NIS? | Notes | Counts
|  |  |  | C | NC | NIS | NP | NTNC
AIRPORT/LARKFIELD/WIKIUP SANITATION ZONE (ALWSZ) | NP | [5 empty] | 1
ALBION MUTUAL WATER COMPANY | C |  |  | 1
ALDERPOINT COUNTY WATER | C |  |  | 1
ALEXANDER VALLEY ACRES WATER COMPANY | C |  |  | 1
ANCIENT REDWOODS R.V. PARK PWS #120 6011 | NC |  |  |  | 1
Anderson Valley Community Services District | NIS | Evaluating feasibility of providing water/ wastewater services, 3.2020 |  |  |  | 1
ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) | C |  |  | 1
ATHENA TERRACE MUTUAL WATER COMPANY | C |  |  | 1
AUSTIN ACRES MUTUAL WATER COMPANY | C |  |  | 1
Austin Creek Mutual (Springhill) | C |  |  | 1
AZALEA GLEN, RV Park and Campgrounds | NC |  |  |  | 1
BAR 717 RANCH, INC. (SUMMER CAMP) | NC |  |  |  | 1
BEACH CREEK MH PARK | C |  |  | 1
BELMONT TERRACE MUTUAL WATER COMPANY | C |  |  | 1
BENBOW W.C. | C |  |  | 1
BENNETT RIDGE MUTUAL WATER COMPANY | C |  |  | 1
BERTSCH OCEANVIEW CSD | C |  |  | 1
BIG LAGOON CSD | C |  |  | 1
BIG LAGOON PARK WATER CO. | C |  |  | 1
BIG RIVER VISTA MUTUAL WATER COMPANY | C |  |  | 1
BIG ROCK C.S.D. | C |  |  | 1
BLUE LAKE, CITY OF | C |  |  | 1
BLUE SPRUCE MOBILE HOME PARK | C |  |  | 1
BODEGA BAY PUBLIC UTILITY DISTRICT | C |  |  | 1
BODEGA WATER COMPANY | C |  |  | 1
BRAND WATER COMPANY | C |  |  | 1
BRANGER MUTUAL WATER COMPANY, INC. | C |  |  | 1
Branscomb Mutual Water Company | C |  |  | 1
BRICELAND C.S.D. | C |  |  | 1
BROOKTRAILS TOWNSHIP CSD | C |  |  | 1
BROOKWOOD MOBILE HOME PARK | C |  |  | 1
BUCHER WATER COMPANY | NTNC | [6 empty] | 1
BUCKTAIL MUTUAL WATER COMPANY | C |  |  | 1
BUD FINE MWC | C |  |  | 1
BURNT RANCH ESTATES Mutual Water Co. | C |  |  | 1
BUTTE MOBILE HOME PARK | C |  |  | 1
CAL ORE MOBILE ESTATES | C |  |  | 1
California American GEYSERVILLE WATER WORKS (PUC) | C |  |  | 1
Green Diamond Resource Company - Korbel | C |  |  | 1
CALIFORNIA-AMERICAN WATER LARKFIELD (PUC) | C |  |  | 1
CALLAHAN WATER DISTRICT | C |  |  | 1
CALPELLA COUNTY WATER DISTRICT | C |  |  | 1
CAMP LIAHONA REDWOODS (YOUTH SUMMER CAMP) | NC |  |  |  | 1
CAMP MEEKER WATER SYSTEM | C |  |  | 1
CAMP ROYANEH | NC |  |  |  | 1
CANON MANOR WATER SYSTEM | C |  |  | 1
CASPAR SOUTH SERVICE COMPANY | C |  |  | 1
Caspar South Water District | NIS | Wastewater | As per Marlene Demery, Caspar South Water District is the wastewater service provider for Caspar. Correspondence by email to demery5@sbcglobal.net, 3.23.20. Contact for Caspar South Water District is: Clouse Steve <sclou@comcast.net> |  |  | 1
CAZADERO WATER COMPANY, INC. | C |  |  | 1
CHINOOK WATER SYSTEM | NC |  |  |  | 1
Church Tree CSD | NIS | Small system |  |  |  | 1
CITY OF ARCATA | C |  |  | 1
CITY OF COTATI | C |  |  | 1
CITY OF ETNA | C |  |  | 1
City of Ferndale | NP | [5 empty] | 1
City of Fortuna WWTP | NIS | Wastewater |  |  |  | 1
CITY OF FORTUNA | C |  |  | 1
CITY OF ROHNERT PARK | C |  |  | 1
CITY OF SANTA ROSA | C |  |  | 1
CLEAR CREEK WATER COMPANY | C |  |  | 1
CLOVERDALE, CITY OF | C |  |  | 1
COLONIAL PARK | C |  |  | 1
COPCO LAKE MWC | C |  |  | 1
COVE MOBILE VILLA | C |  |  | 1
COVELO C.S.D. | NIS | Wastewater |  |  |  | 1
COVELO MOBILE HOME PARK | C |  |  | 1
COVINGTON MILL MWC-DIVISION B | C |  |  | 1
Creekside Cabins & RV Resort | C |  |  | 1
CRESCENT CITY, CITY OF | C |  |  | 1
CRIVELLI'S WATER SYSTEM | NC |  |  |  | 1
DEL NORTE COUNTY COMMUNITY SERVICE AREA | NIS | Wastewater |  |  |  | 1
DELORES LANE WATER SYSTEM | C |  |  | 1
Dolphin Isle Marina | C |  |  | 1
DORRIS, CITY OF | C |  |  | 1
Dos Rios Mutual Water Company | NP | [5 empty] | 1
DOWNTOWN GRATON MUTUAL WATER SYSTEM | C |  |  | 1
EAST AUSTIN CREEK MUTUAL WATER COMPANY | NC |  |  |  | 1
EL CRYSTAL MOBILE HOME PARK | C |  |  | 1
EL PORTAL MOBILE ESTATES | C |  |  | 1
ELK COUNTY WATER DISTRICT | C |  |  | 1
EMERALD FOREST | NC |  |  |  | 1
END-O-VALLEY MUTUAL WATER COMPANY | C |  |  | 1
EUREKA, CITY OF, ELK RIVER WWTP | NIS | Wastewater |  |  |  | 1
EUREKA, CITY OF | C |  |  | 1
FARMER WATER SYSTEM | NC |  |  |  | 1
FERNDALE - DEL ORO WATER CO. | C |  |  | 1
FIELDBROOK GLENDALE C.S.D. | C |  |  | 1
FIRCREST MUTUAL WATER COMPANY | C |  |  | 1
Forestville Water District | C |  |  | 1
FORT BRAGG MUNICIPAL IMP DISTRICT | NIS | Wastewater |  |  |  | 1
Fort Bragg City WWTP | NIS | Wastewater |  |  |  | 1
FORT BRAGG, CITY OF | C |  |  | 1
FORT JONES, TOWN OF | C |  |  | 1
GARBERVILLE SANITARY DISTRICT | C |  |  | 1
GASQUET C.S.D. | C |  |  | 1
GEYSERVILLE SANITATION ZONE | NIS | Wastewater |  |  |  | 1
GILL CREEK MUTUAL WATER COMPANY | C |  |  | 1
GOLDEN BEAR RV PARK | NC |  |  |  | 1
Graton CSD | NP | [5 empty] | 1
GRATON MUTUAL (GREEN VALLEY HOA) | C |  |  | 1
GREEN ACRES TRAILER PARK | NC |  |  |  | 1
GRENADA SANITARY DISTRICT | C |  |  | 1
Gualala Community Services District | NP | [5 empty] | 1
HAPPY ACRES MUTUAL BENEFIT WATER SYSTEM | C |  |  | 1
HAPPY CAMP C.S.D. | C |  |  | 1
HAPPY CAMP S.D. | NIS | Wastewater |  |  |  | 1
HAWKINS WATER CO-CAL WATER SERVICE (PUC) | C |  |  | 1
HEALDSBURG, CITY OF | C |  |  | 1
HEIGHTS MUTUAL WATER COMPANY | C |  |  | 1
HERITAGE HOUSE RESORT AND SURFWOOD MUTUAL WATER CORP. | NTNC | [6 empty] | 1
HILLS RANCH MUTUAL WATER COMPANY | C |  |  | 1
HILTON MUTUAL WATER COMPANY | C |  |  | 1
HOLLAND HEIGHTS MUTUAL WATER COMPANY | C |  |  | 1
HOLLY RANCH VILLAGE | C |  |  | 1
HOPLAND PUBLIC UTILITY DISTRICT | C |  |  | 1
HORNBROOK C.S.D. | C |  |  | 1
Hussey Ranch Corporation (HRC) C.S.D. | C |  |  | 1
HUCKLEBERRY MUTUAL WATER COMPANY | C |  |  | 1
HUMBOLDT BAY MWD | C |  |  | 1
HUMBOLDT C.S.D. | C |  |  | 1
Humboldt County RID #1, Shelter Cove POTW | C |  |  | 1
HUNTER VALLEY CSD | C |  |  | 1
HYDESVILLE CO. W.D. | C |  |  | 1
INDIAN CREEK TRAILER PARK | C |  |  | 1
IRISH BEACH WATER DISTRICT | C |  |  | 1
JACOBY CREEK CSD - combined with City of Arcata | C |  |  | 1
JED SMITH HOMEOWNERS ASSN. | C |  |  | 1
JUNIPER CREEK ESTATES | C |  |  | 1
KAMP KLAMATH CORP. | NC |  |  |  | 1
KELLY MUTUAL WATER COMPANY | C |  |  | 1
KLAMATH C.S.D. (Del Norte Community Development) | C |  |  | 1
KLAMATH CAMPER CORRAL | NC |  |  |  | 1
KLAMATH RIVER RV PARK | NC |  |  |  | 1
LAKE SHASTINA C.S.D | C |  |  | 1
LAKE VIEW MUTUAL WATER CO. | C |  |  | 1
LAS PALMAS MOBILE HOME PARK | C |  |  | 1
LAYTONVILLE COUNTY WATER DISTRICT | C |  |  | 1
LEISURE MOBILE HOME PARK | C |  |  | 1
LEWISTON Community Services District | C |  |  | 1
LITTLE LAKE MOBILE HOME PARK | C |  |  | 1
LOLETA C.S.D. | C |  |  | 1
LONE PINE MUTUAL WATER COMPANY | C |  |  | 1
MACDOEL WATERWORKS | NIS | Small system, called 541.882.8543 on 3.20.20 and spoke with Sarah, who told me to call back and speak with Terri Bennett. 3.23.20, spoke with Lisa in depth and she will ask Vanessa or Terri to call me back re: system. It is still operating, but the users are Spanish speakers, so there is a language barrier. |  |  |  | 1
MADRONA MANOR 140330 | NTNC | [6 empty] | 1
MADRONE MUTUAL WATER COMPANY | C |  |  | 1
MAGIC MOUNTAIN MUTUAL WATER COMPANY | C |  |  | 1
MANILA COMMUNITY SERVICES DIST. | C |  |  | 1
MCCLOUD C.S.D. | C |  |  | 1
MARK WEST ACRES MWC | C |  |  | 1
MARK WEST MEADOWS MUTUAL WATER CO. | C |  |  | 1
MCKINLEYVILLE C.S.D. | C |  |  | 1
MEADOW ESTATES MUTUAL | C |  |  | 1
MELITA HEIGHTS MUTUAL WATER COMPANY | C |  |  | 1
MENDOCINO CITY C.S.D. | NP |  | City oversees well use with GWMP |  |  |  | 1
MENDOCINO COUNTY WATER WORKS DISTRICT NO. II | NIS | Likely only wastewater; is not included in the County LAFCO SOI or MSR reports. It is included in the Mendocino County GP map of entities that provide wastewater service, but not included in the map of entities that provide water services. |  |  |  | 1
MICHELE MUTUAL WATER COMPANY | C |  |  | 1
MILL CREEK M.W.C. | C |  |  | 1
MILLVIEW COUNTY WATER DISTRICT | C |  |  | 1
MIRANDA C.S.D. | C |  |  | 1
MOBILE HOME ESTATES | C |  |  | 1
MONTAGUE, CITY OF | C |  |  | 1
MONTAGUE WATER CONSERVATION DISTRICT | NIS | Irrigation and wholesale to City | phoned 3.23.20 (530.459.3371) provide irrigation water and wholesale water to City of Montague |  |  | 1
Montair Subdivision Homeowners Association | NIS | Wastewater |  |  |  | 1
MOONSTONE HEIGHTS MWA | C |  |  | 1
MOUNT WESKE ESTATES MUTUAL WATER COMPANY | NIS | Too small for SDWIS |  |  |  | 1
MOUNTAIN VIEW MOBILE ESTATES, LLC | C |  |  | 1
MYERS FLAT M.W.S. INC. | C |  |  | 1
NEVES FAMILY TRUST WATER SYSTEM | NC |  |  |  | 1
NEWELL COUNTY WATER DISTRICT | C |  |  | 1
NOEL HEIGHTS-CAL WATER SERVICE (PUC) | C |  |  | 1
NORTH GUALALA WATER COMPANY | C |  |  | 1
NORTH STAR MOBILE HOME PARK | C |  |  | 1
NOYO HARBOR DISTRICT | NIS | The primary mission of the Noyo Harbor District is to ensure that the Noyo Harbor District is a viable operational and financial entity, providing boating and marine related opportunities for the public. |  |  |  | 1
OAK VALLEY ACRES P.O.A. (requested no further contact 2017/18) | C |  | This system should only be carried over, never contacted. They requested no further contact from NCRP in 2018/19 | 1
OCCIDENTAL COMMUNITY SERVICES DISTRICT | C |  |  | 1
OCCIDENTAL COUNTY SANITATION DISTRICT | NP | [5 empty] | 1
Odd Fellows Recreation Club | C |  |  | 1
ORICK C.S.D. | C |  |  | 1
ORLEANS C.S.D. | C |  |  | 1
ORLEANS MUTUAL WATER CO. | C |  |  | 1
PACIFIC REEFS WATER DISTRICT | NC |  |  |  | 1
PALMER CREEK CSD | C |  |  | 1
PALOMINO ESTATES M.W.C. | C |  |  | 1
PALOMINO LAKES MUTUAL WATER CO. | C |  |  | 1
PARK ROYAL MUTUAL WATER | C |  |  | 1
PATRICK CREEK COMMUNITY SERVICE DISTRICT | NIS | The District originally had its own water system. However, in 1973, the Patrick Creek Community Services District (PCCSD) transferred interest in the distribution system to the McKinleyville Community Services District where water obtained from the HBMWD is distributed. The water system currently serves 17 homes, with a total capacity of 18 homes. One household has two lots, and the rest are single lots. With the exception of the possibility of the double lot ownership, the district is at capacity. Still in Mendocino County GP documents, leave system in list for time being. |  |  |  | 1
PHILLIPSVILLE C.S.D. | C |  |  | 1
Pine Cove RV Park | C |  |  | 1
PINE GROVE Mobile Home PARK | C |  |  | 1
PINE HILL TERRACE MOBILE HOME PARK | C |  |  | 1
PINE MOUNTAIN MUTUAL WATER CO. | C |  |  | 1
PLAZA MOBILE HOME PARK | C |  |  | 1
POINT ARENA WATER WORKS | C |  |  | 1
Point Arena WWTP | NIS | Wastewater |  |  |  | 1
Point Arena Lighthouse Keepers | NC |  |  |  | 1
POINT CABRILLO HIGHLANDS | C |  |  | 1
POINT OF VIEW MUTUAL WATER CO | C |  |  | 1
RAINS CREEK WATER DISTRICT | C |  |  | 1
RANCHO DEL PARADISO-CAL WATER SVC (PUC) | C |  |  | 1
RANDAL'S RANCHETTE MUTUAL WATER CO. | C |  |  | 1
REDCREST WATER WORKS | C |  |  | 1
REDWAY C.S.D. | C |  |  | 1
REDWOOD HEIGHTS WATER ASSOCIATION | C |  |  | 1
REDWOOD PARK C.S.D. | C |  |  | 1
REDWOOD VALLEY COUNTY WATER DISTRICT | C |  |  | 1
Reservation Ranch | C |  |  | 1
RESORT IMPRVMT. DIST. #1 | C |  |  | 1
White Deer Lodge Water System (formerly RIDGE WATER SYSTEM) | NC |  |  |  | 1
RIDGEWOOD WATER SYSTEM | C |  |  | 1
RIEBLI MUTUAL WATER COMPANY | C |  |  | 1
RINCON VALLEY MOBILE ESTATES | C |  |  | 1
RIO DELL, CITY OF | C |  |  | 1
(Russian) RIVER ESTATES MUTUAL WATER COMPANY | C |  |  | 1
Riverbend Mobile Home Park | C |  |  | 1
RIVERSIDE CSD | C |  |  | 1
ROGINA WATER COMPANY INC. | C |  |  | 1
ROLLING OAKS ROAD ASSOCIATION | C |  |  | 1
ROSELAND MOBILE HOME PARK | C |  |  | 1
RUSH CREEK MUTUAL WATER SYSTEM | C |  |  | 1
RUSSIAN RIVER COUNTY SANITATION DISTRICT | NP | [5 empty] | 1
RUSSIAN RIVER MUTUAL WATER CO. | C |  |  | 1
RUTH LAKE MARINA AND RECREATION AREA | NC |  |  |  | 1
SALYER HEIGHTS W.S., INC | C |  |  | 1
SALYER MUTUAL WC (FORMERLY RIVERVIEW AC) | C |  |  | 1
SANTA ROSA MOBILE ESTATES | C |  |  | 1
SAWYER S BAR WORK CENTER (formerly SAWYERS BAR COUNTY WATER DISTRICT) | NC |  |  |  | 1
Scotia CSD | C |  |  | 1
SEA RANCH SANITATION ZONE | NP | [5 empty] | 1
SEA RANCH WATER COMPANY,THE (PUC) | C |  |  | 1
SEAFAIR ROAD AND WATER COMPANY | C |  |  | 1
SEAWOOD ESTATES MUTUAL WATER | C |  |  | 1
SEBASTOPOL, CITY OF | C |  |  | 1
SEQUOIA WATER COMPANY | NC |  |  |  | 1
SERENO DEL MAR WATER CO. | C |  |  | 1
SEYMOUR'S MUTUAL WATER SYSTEM | C |  |  | 1
SHADOW MOUNTAIN MHP | C |  |  | 1
SHAMROCK MOBILE HOME PARK | C |  |  | 1
SHASTA VIEW HEIGHTS OWNERS ASSOCIATION | C |  |  | 1
SHASTINA MOBILE ESTATES | C |  |  | 1
SHORELANDS ROAD & WATER COMPANY | C |  |  | 1
SISKIYOU CO. ROLLING HILLS MWC | C |  |  | 1
SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system) | C |  |  | 1
Six Acres Water Company | C |  |  | 1
SMITH RIVER C.S.D. | C |  |  | 1
SONOMA COUNTY CSA 41-FITCH MOUNTAIN | C |  |  | 1
SONOMA COUNTY CSA 41-FREESTONE | C |  |  | 1
SONOMA COUNTY CSA 41-JENNER | C |  |  | 1
SONOMA COUNTY CSA 41-SALMON CREEK | C |  |  | 1
SONOMA COUNTY MUTUAL WATER COMPANY | C |  |  | 1
SONOMA COUNTY WATER AGENCY | C |  |  | 1
SONOMA MOUNTAIN COUNTY WATER DISTRICT | C |  |  | 1
SONOMA WEST HOLDINGS NORTH PLANT | NTNC | [6 empty] | 1
SOUNDS OF THE SEAS W. S. | NC |  |  |  | 1
SOUTH CLOVERDALE WATER COMPANY | C |  |  | 1
SOUTH PARK COUNTY SANITATION DISTRICT | NIS | Wastewater |  |  |  | 1
STEWARTS POINT WATER SYSTEM | NC |  |  |  | 1
STONEGATE MOBILE HOME PARK | C |  |  | 1
SUMMIT VIEW RANCH MUTUAL WATER CO. | C |  |  | 1
SUNRISE MOUNTAIN MUTUAL WATER COMPANY | C |  |  | 1
SUNSET PARK COMMUNITY | C |  |  | 1
SURFWOOD MUTUAL WATER CORPORATION | C |  |  | 1
SWEETWATER SPRINGS CWD - GUERNEVILLE | C |  |  | 1
SWEETWATER SPRINGS CWD - MONTE RIO | C |  |  | 1
SYLVAN HARBOR TRAILER PARK | NC |  |  |  | 1
TENNANT C.S.D. | C |  |  | 1
TERRACE VIEW WATER SYSTEM | C |  |  | 1
TIMBER COVE COUNTY WATER DISTRICT | C |  |  | 1
TREASURE CREEK WOODS MWC | C |  |  | 1
Trinidad Extended Stay | C | SDWIS system # is 1200706; used to be midway |  | 1
TRINIDAD, CITY OF | C |  |  | 1
TRINITY CENTER M.W.C. . | C |  |  | 1
TRINITY CO. W.W. DIST #1 | NP | [5 empty] | 1
TRINITY KNOLLS MUTUAL WATER COMPANY | C |  |  | 1
TRINITY VILLAGE MUTUAL WATER CO. | C |  |  | 1
TRIUMPH LIFE CAMP (TLC) YOUTH SUMMER CAMP | NC |  |  |  | 1
TULELAKE, CITY OF | C |  |  | 1
Twin Hills Vineyard (formerly TWIN HILLS MUTUAL WATER COMPANY) | NC | Is called "Twin Hills Vineyard" in SDWIS now with the same SDWIS # 4900604 |  |  | 1
Ukiah Valley Sanitation District | NIS | Wastewater |  |  |  | 1
UKIAH, CITY OF | C |  |  | 1
Ukiah City WWTP | NIS | Wastewater |  |  |  | 1
Upper Russian River Water Agency (formerly MENDOCINO COUNTY RUSSIAN RIVER FLOOD CONTROL AND WATER CONSERVATION DISTRICT) | NIS | Flood Control/ Irrigation |  |  |  | 1
VALLEY FORD WATER ASSOCIATION | C |  |  | 1
VINEHILL VISTA MUTUAL WATER COMPANY | C |  |  | 1
WADDINGTON W.W. | C |  |  | 1
WAYSIDE GARDENS MOBILE HOME PARK | C |  |  | 1
WEAVERVILLE C.S.D. | C |  |  | 1
WEAVERVILLE S.D. | NIS | Wastewater |  |  |  | 1
WEED, CITY OF | C |  |  | 1
WEOTT C.S.D. | C |  |  | 1
WENDELL WATER COMPANY (PUC) / Wendell Lane Mutual Water Company | C |  |  | 1
WEST PARK PROPERTIES | C |  |  | 1
WEST WATER COMPANY (PUC) | C |  |  | 1
WESTERN MOBILE HOME PARK | C |  |  | 1
WESTHAVEN C.S.D. | C |  |  | 1
WESTPORT COUNTY WATER DISTRICT | C |  |  | 1
Wildwood Campground | C |  |  | 1
WILDWOOD RETREAT (WILDWOOD CONSERVATION FOUNDATION) | NC |  |  |  | 1
Willits City WWTP | NIS | Wastewater |  |  |  | 1
WILLITS, CITY OF | C |  |  | 1
WILLOW COUNTY WATER DISTRICT | C |  |  | 1
WILLOW CREEK C.S.D. | C |  |  | 1
WILLOWSIDE MUTUAL WATER COMPANY | C |  |  | 1
WILSHIRE HEIGHTS MUTUAL WATER COMPANY | C |  |  | 1
WINDSOR, TOWN OF | C |  |  | 1
Woods, The (Mendocino) | C |  |  | 1
WOODSIDE RV PARK & CAMPGROUND | C |  |  | 1
YREKA, CITY OF | C |  |  | 1
YULUPA MUTUAL WATER COMPANY | C |  |  | 1
|  |  | 308 | 241 | 28 | 25 | 10 | 4
|  |  | 1 | 78.25% | 9.091% | 8.117% | 3.247% | 1.299%

## Spreadsheet Metadata
NCRP DACTI 2018 Needs Assessment Table
Fields Metadata and Methods
Community System (C): According to the State of California, a Community Water System (C) is a public water system that serves at least 15 service connections used by yearlong residents or regularly serves at least 25 yearlong residents. This category includes municipal water systems and mutual water associations. For this spreadsheet and the associated report, we expand this definition of community water systems to also include those categorized as "state small water systems:" systems that provide piped water to the public for human consumption and serve at least five, but not more than 14, service connections and do not regularly serve drinking water to more than an average of 25 individuals daily for more than 60 days out of the year.
2017/18 Survey Response: “y” indicates that a representative of the system filled out the NCRP 2017 Water Needs Survey.
2014 Survey Response: “y” indicates that a representative of the system filled out the NCRP 2014 Water Needs Survey.
Water/ Wastewater System: The name of the water or wastewater provider. Sources for this information include county data, State Drinking Water System Information System (SDWIS), and survey responses.
Type: Entity organizational structure: City, CSD, Public Utility, Municipal Improvement, Mutual, Tribal Organization, Water District, Other, etc. NCRP in-house data.
Address: System’s physical address. Data sources include survey responses, SDWIS, and county planning departments.
System has paid FT staff: “y” indicates that a survey respondent or LAFCO Sphere of Influence report has indicated the system has paid full-time staff. “n” indicates that the system does not have paid full-time staff; it might have part-time staff, use a consultant, or rely on volunteers.
System has identified itself as in need of financial assistance: ”y” indicates that the representative of the system taking the 2017 survey responded in the affirmative. “n” indicates that the representative of the system taking the 2017 survey responded negatively.
System has a current Emergency Response Plan: “y’ indicates the 2017/18 survey respondent said that the system has a current ERP. “n” indicates that the 2017/18 survey respondent said that the system does not have a current ERP.
# Hookups: The number of hookups to external sources – homes, businesses, etc. These data were obtained from SDWIS and 2018 survey respondents.
# Hookups Categories: Using the data from # Hookups field, responses were categorized for analysis and visual presentation.
Rate Structure described: 2018 survey respondents chose from rate structure categories and/ or provided an open ended response.
Rate Structure categorized: Open ended responses from the “Rate Structure described” field were categorized for analysis and visual presentation.
Description of involvement with NCRP: 2018 survey respondents chose from involvement categories and/ or provided an open ended response.
Involvement with NCRP categories: Open ended responses from the “Description of involvement with NCRP” field were categorized for analysis and visual presentation. Additionally, NCRP records were reviewed to verify that respondents’ answers reflected the system’s involvement with the NCRP, not their personal experience. In cases where the respondent was unfamiliar with the NCRP, but the system had interacted with the NCRP in the past, responses were changed to reflect that interaction.
Has submitted project to NCRP: NCRP records (NCRP Plan, Phase IV, Appendix B) were reviewed to populate this field. “Funded” indicates that the system applied for IRWM funding through the NCRP and received funding; “Unfunded” indicates the system applied for, but did not receive IRWM funding through the NCRP.
Level of concern for system on the following topics (0 = no concern, 1 = moderate, 2 = strong, 3 = extreme, N/A = N/A "blank" = no response): These responses were provided by 2018 survey respondents.
Level of need for technical assistance (0 = no concern, 1 = moderate, 2 = strong, 3 = extreme, N/A = N/A "blank" = no response): These responses were provided by 2018 survey respondents.
Community: Name of the community or location of the neighborhood the system serves. Survey respondents and county documents provided these data.
County: County in which the system is located. These data were provided by SDWIS and county records.
IRWM Region: The IRWM region for all systems is the North Coast.
MHI: Median Household Income for the community in which the system is located. The MHI was determined using a geographic information system (GIS), median household income (MHI) census tract and block group data derived from the US Census Bureau's American Community Survey (ACS) compiled for the 5-year period 2012-2016. These data were made available by DWR on the Resources - Disadvantaged Communities (DAC) Mapping Tool webpage at https://gis.water.ca.gov/app/dacs/ After GIS analysis, 18 systems did not have MHI data because of lack of address of system or other inconsistencies with the data. These systems were looked up manually and assigned the MHI that other systems in the same area had. For example, Anderson Valley CSD was assigned the same MHI as Meadow Estates Mutual, which is also located in Boonville, CA.
Tribal Community: “y” indicates that the community the system serves is a Tribal community. “n” indicates that the community the system serves is not a Tribal community, "p" indicates that the system includes a Tribal community in its service area. All Tribal systems were removed from the Disadvantaged Community Analysis and analyzed separately.
Population: The population of the community in which the system is located, or the specific population served by the system for neighborhood systems for which data was available. Data were obtained from US Census Bureau's American Community Survey (ACS) compiled for the 5-year period 2012-2016, county planning documents, and 2018 survey responses.
Primary source of water: Indicates whether the primary water source is groundwater (GW), surface water (SW), groundwater under the influence of surface water (GU), or purchased from a wholesale supplier(GWP or SWP). Blanks indicate lack of data or that the system is not a water supplier. Data were obtained from SDWIS.
Specifics about water source(s): Number of groundwater wells, surface water source, or entity from whom water is purchased. Data were obtained from SDWIS.
Estimate Number of private wells: Estimated number of private wells located in community. Data obtained from county documents.
Estimate number of public wells: Number of public wells used by the system. Data obtained from SDWIS.
Water Treatment Information: Treatment used to make water potable. Data obtained from survey responses, county documents, and system web pages.
Drinking water issues & system status: Current drinking water system infrastructure, state of the infrastructure and any issues. Data obtained from 2018 survey responses and county documents.
DW System Status Categories: Open ended responses from the “Drinking water issues & system status” field were categorized for analysis and visual presentation. Categories are: adequate; fair condition/ upgrades planned; good condition; interest/ plan to consolidate; poor condition; regulatory – septic; storage capacity insufficient.
Anything (other than AS) unusual or problematic about water: Irregularities associated with water source such as taste, odor, or contamination. Data obtained from 2018 survey.
DDW Rank: System priority rank for assistance by the Department of Drinking Water. Data obtained from the Drinking Water State Revolving Fund Criteria for Public Health Need.
Category A - Immediate Health Risk
Category B - Untreated or At-Risk Sources
Category C - Compliance or Shortage Problems
Category D - Inadequate Reliability
Category E - Secondary Risks
Category F - Other Projects
DDW Violation Type: Description of drinking water system violation(s). Data obtained from SWRCB.
DDW Action Date: Date of drinking water system violation(s). Data obtained from SWRCB.
SWRCB Rank: System priority rank for assistance by the State Water Resources Control Board. Data obtained from the Clean Water State Revolving Fund Criteria for Public Health/ Water Quality.
Class A - Public Health Problems
Class B - Pollution of Impaired Water Bodies
Class C - Compliance with requirements or Water Recycling Projects
Class D - Projects Serving as Preventative Measures
Class E - Other Projects
RWQCB Decision Type: Type of decision – whether a notice of violation, administrative civil liability, failure to submit, etc. Data obtained from North Coast Regional Water Quality Control Board (NCRWQCB).
RWQCB Date: Date of NCRWQCB action. Data obtained from NCRWQCB.
Type of Wastewater System: Wastewater system type: sewer, septic, or septic with central collection. Data obtained from county documents and 2018 survey responses.
Sewer System Issues: System status and any existing conditions. Data obtained from survey responses and county documents.
Stormwater/ Urban water runoff/ flood management issues: Status of stormwater and flood management. Data obtained from survey responses and county documents.
EPA Affordability Criteria Threshold: Calculates the percentage of MHI represented by average water bill, sewer bill, or both based on criteria established by the US EPA. The threshold beyond which affordability is considered impacted is 2.5% of MHI for water, 2% of MHI for wastewater, and 4.5% for both. Data obtained from 2018 survey responses and county planning documents.

## Lists
Wastewater | # Hookups | Rate Structure | Monthly Water/ Wastewater Bill | NCRP Participation | Water Systems Issues Categories | Wastewater Systems Issues Categories | Submitted Proposal to NCRP | SDWIS Water System Classification
sewer | 0 - 15 | Contained in rental fees/ camp cost | $0 - $50 | Familiar | Adequate | Adequate | Funded | C | C - Community | Serves at least 15 service connections used by year-round residents or regularly serves 25 year-round residents.
septic | 16 - 50 | Flat rate - monthly or annual | $51 - $100 | Familiar; infrequent participation | Fair condition/ Upgrades planned/ identified | Fair condition/ Upgrades planned/ identified | Unfunded | NIS | NIS - Not in SDWIS
septic - centralized collection | 51 - 100 | Flat rate + variable usage charge | $101 - $150 | Familiar; lack resources to participate | Good condition | Good condition |  | NP | NC - Transient Non-Community | Regularly serves at least 25 non-residential individuals (transient) during 60 or more days per year.
percolation ponds | 101 - 250 | Increasing block | > $150 | Familiar; not a participant | Poor condition | Interest/ plan to consolidate |  | NTNC | NP - Non-Public
| 251 - 500 | No charge |  | Familiar; regular participant | Storage capacity insufficient | Poor condition |  | NC | NTNC - Non-Transient Non-Community | Serves at least the same 25 non-residential individuals during 6 months of the year.
| 501 - 1,000 | Seasonal |  | Unfamiliar; interested | Uncertain water supply | Regulatory - septic
| 1,001 - 5,000 | Subsidized |  | Unfamiliar; disinterested |  | Storage capacity insufficient
| > 5,000 | Uniform rate schedule |  | Unfamiliar; lack resources to investigate/participate

## Contaminants of Concern
NC Disadvantaged Community Systems using Groundwater that has tested > MCL for Arsenic |  |  | North Coast Resource Partnership Plan: Healthy Communities, Functional Ecosystems, & Vibrant Economies, September 2019
Water/ Wastewater System | Arsenic |  | Table 4. North Coast Systems with Exceedences of Arsenic in Groundwater *Exceeds EPA Affordability Criteria
| Treatment Method | Count | Systems | Disadvantaged/ Severely Disadvantaged
ALBION MUTUAL WATER COMPANY |  |  | LAYTONVILLE COUNTY WATER DISTRICT * | SD
ALDERPOINT COUNTY WATER |  |  | MOUNT WESKE ESTATES MUTUAL WATER COMPANY | D
Anderson Valley Community Services District |  |  | PALOMINO ESTATES M.W.C. | SD
ARMSTRONG VALLEY-CAL WATER SERVICE (PUC) |  |  | SHAMROCK MOBILE HOME PARK | D
ATHENA TERRACE MUTUAL WATER COMPANY |  |  | WESTERN MOBILE HOME PARK | SD
Austin Creek Mutual (Springhill) |  |  | WINDSOR, TOWN OF | D
BAR 717 RANCH, INC. (SUMMER CAMP)
BEACH CREEK MH PARK
BENBOW W.C.
BENNETT RIDGE MUTUAL WATER COMPANY
BERTSCH OCEANVIEW CSD
BIG LAGOON CSD
BIG LAGOON PARK WATER CO.
BIG RIVER VISTA MUTUAL WATER COMPANY
BIG ROCK C.S.D.
BLUE LAKE, CITY OF
BRAND WATER COMPANY
BRANGER MUTUAL WATER COMPANY, INC.
Branscomb Mutual Water Company
BRICELAND C.S.D.
BROOKTRAILS TOWNSHIP CSD
BROOKWOOD MOBILE HOME PARK
BUCKTAIL MUTUAL WATER COMPANY
BUD FINE MWC
BURNT RANCH ESTATES Mutual Water Co.
BUTTE MOBILE HOME PARK
CAL ORE MOBILE ESTATES
California American GEYSERVILLE WATER WORKS (PUC)
Green Diamond Resource Company - Korbel
CALIFORNIA-AMERICAN WATER LARKFIELD (PUC)
CALLAHAN WATER DISTRICT
CALPELLA COUNTY WATER DISTRICT
CANON MANOR WATER SYSTEM
CASPAR SOUTH SERVICE COMPANY
Caspar South Water District
CAZADERO WATER COMPANY, INC.
Church Tree CSD
CITY OF ARCATA
CITY OF COTATI
CITY OF ETNA
City of Ferndale
City of Fortuna WWTP
CITY OF FORTUNA
CITY OF SANTA ROSA
COPCO LAKE MWC
COVE MOBILE VILLA
COVELO C.S.D.
COVELO MOBILE HOME PARK
COVINGTON MILL MWC-DIVISION B
Creekside Cabins & RV Resort
CRESCENT CITY, CITY OF
DEL NORTE COUNTY COMMUNITY SERVICE AREA
DELORES LANE WATER SYSTEM
Dolphin Isle Marina
DORRIS, CITY OF
Dos Rios Mutual Water Company
EAST AUSTIN CREEK MUTUAL WATER COMPANY
EL CRYSTAL MOBILE HOME PARK
EL PORTAL MOBILE ESTATES
ELK COUNTY WATER DISTRICT
END-O-VALLEY MUTUAL WATER COMPANY
EUREKA, CITY OF, ELK RIVER WWTP
EUREKA, CITY OF
FERNDALE - DEL ORO WATER CO.
FIELDBROOK GLENDALE C.S.D.
Forestville Water District
FORT BRAGG MUNICIPAL IMP DISTRCT
Fort Bragg City WWTP
FORT BRAGG, CITY OF
FORT JONES, TOWN OF
GARBERVILLE SANITARY DISTRICT
GASQUET C.S.D.
GEYSERVILLE SANITATION ZONE
GILL CREEK MUTUAL WATER COMPANY
GRENADA SANITARY DISTRICT
Gualala Community Services District
HAPPY CAMP C.S.D.
HAPPY CAMP S.D.
HEIGHTS MUTUAL WATER COMPANY
HILLS RANCH MUTUAL WATER COMPANY
HILTON MUTUAL WATER COMPANY
HOLLAND HEIGHTS MUTUAL WATER COMPANY
HOLLY RANCH VILLAGE
HOPLAND PUBLIC UTILITY DISTRICT
HORNBROOK C.S.D.
Hussey Ranch Corporation (HRC) C.S.D.
HUCKLEBERRY MUTUAL WATER COMPANY
HUMBOLDT BAY MWD
HUMBOLDT C.S.D.
Humboldt County RID #1, Shelter Cove POTW
HUNTER VALLEY CSD
INDIAN CREEK TRAILER PARK
IRISH BEACH WATER DISTRICT
JACOBY CREEK CSD - combined with City of Arcata
JED SMITH HOMEOWNERS ASSN.
JUNIPER CREEK ESTATES
KLAMATH C.S.D. (Del Norte Community Development)
LAKE SHASTINA C.S.D
LAYTONVILLE COUNTY WATER DISTRICT | Coagulation/ oxidation | 1
LEWISTON Community Services District
LITTLE LAKE MOBILE HOME PARK
LOLETA C.S.D.
MACDOEL WATERWORKS
MADRONE MUTUAL WATER COMPANY
MAGIC MOUNTAIN MUTUAL WATER COMPANY
MANILA COMMUNITY SERVICES DIST.
MCCLOUD C.S.D.
MARK WEST ACRES MWC
MARK WEST MUTUAL WATER CO.
MCKINLEYVILLE C.S.D.
MEADOW ESTATES MUTUAL
MELITA HEIGHTS MUTUAL WATER COMPANY
MENDOCINO CITY C.S.D.
MENDOCINO COUNTY WATER WORKS DISTRICT NO. II
MICHELE MUTUAL WATER COMPANY
MILL CREEK M.W.C.
MILLVIEW COUNTY WATER DISTRICT
MIRANDA C.S.D.
MOBILE HOME ESTATES
MONTAGUE, CITY OF
MONTAGUE WATER CONSERVATION DISTRICT
Montair Subdivision Homeowners Association
MOONSTONE HEIGHTS MWA
MOUNT WESKE ESTATES MUTUAL WATER COMPANY | working with SWRCB (2019) | 1
MOUNTAIN VIEW MOBILE ESTATES, LLC
MYERS FLAT M.W.S. INC.
NEWELL COUNTY WATER DISTRICT
NOEL HEIGHTS-CAL WATER SERVICE (PUC)
NORTH GUALALA WATER COMPANY
OAK VALLEY ACRES P.O.A.
Odd Fellows Recreation Club
ORICK C.S.D.
ORLEANS C.S.D.
ORLEANS MUTUAL WATER CO.
PACIFIC REEFS WATER DISTRICT
PALMER CREEK CSD
PALOMINO ESTATES M.W.C. | Triple media filtration | 1
PALOMINO LAKES MUTUAL WATER CO.
PARK ROYAL MUTUAL WATER
PATRICK CREEK COMMUNITY SERVICE DISTRICT
PHILLIPSVILLE C.S.D.
Pine Cove RV Park
PINE GROVE Mobile Home PARK
PINE MOUNTAIN MUTUAL WATER CO.
PLAZA MOBILE HOME PARK
POINT ARENA WATER WORKS
Point Arena WWTP
RAINS CREEK WATER DISTRICT
RANDAL'S RANCHETTE MUTUAL WATER CO.
REDCREST WATER WORKS
REDWAY C.S.D.
REDWOOD HEIGHTS WATER ASSOCIATION
REDWOOD PARK C.S.D.
Reservation Ranch
RESORT IMPRVMT. DIST. #1
RIDGEWOOD WATER SYSTEM
RIEBLI MUTUAL WATER COMPANY
RINCON VALLEY MOBILE ESTATES
RIO DELL, CITY OF
(Russian) RIVER ESTATES MUTUAL WATER COMPANY
Riverbend Mobile Home Park
RIVERSIDE CSD
ROLLING OAKS ROAD ASSOCIATION
ROSELAND MOBILE HOME PARK
RUSH CREEK MUTUAL WATER SYSTEM
RUSSIAN RIVER COUNTY SANITATION DISTRICT
SALYER HEIGHTS W.S., INC
SALYER MUTUAL WC (FORMERLY RIVERVIEW AC)
SANTA ROSA MOBILE ESTATES
SAWYERS BAR COUNTY WATER DISTRICT
Scotia CSD
SEAFAIR ROAD AND WATER COMPANY
SEAWOOD ESTATES MUTUAL WATER
SERENO DEL MAR WATER CO.
SEYMOUR'S MUTUAL WATER SYSTEM
SHADOW MOUNTAIN MHP
SHAMROCK MOBILE HOME PARK | Precipitative process using FeCl3 | 1
SHASTA VIEW HEIGHTS OWNERS ASSOCIATION
SHASTINA MOBILE ESTATES
SHORELANDS ROAD & WATER COMPANY
SISKIYOU CO. ROLLING HILLS MWC
SISKIYOU CO.SERVICE AREA #5/CARRICK (functionally part of City of Weed's water system)
Six Acres Water Company
SMITH RIVER C.S.D.
SONOMA COUNTY CSA 41-FITCH MOUNTAIN
SONOMA COUNTY CSA 41-FREESTONE
SONOMA COUNTY CSA 41-JENNER
SONOMA COUNTY CSA 41-SALMON CREEK
SONOMA COUNTY MUTUAL WATER COMPANY
SONOMA COUNTY WATER AGENCY
SONOMA MOUNTAIN COUNTY WATER DISTRICT
SOUTH CLOVERDALE WATER COMPANY
SOUTH PARK COUNTY SANITATION DISTRICT
SUMMIT VIEW RANCH MUTUAL WATER CO.
SUNRISE MOUNTAIN MUTUAL WATER COMPANY
SUNSET PARK COMMUNITY
SURFWOOD MUTUAL WATER CORPORATION
SWEETWATER SPRINGS CWD - GUERNEVILLE
SWEETWATER SPRINGS CWD - MONTE RIO
TENNANT C.S.D.
TERRACE VIEW WATER SYSTEM
TIMBER COVE COUNTY WATER DISTRICT
TREASURE CREEK WOODS MWC
Trinidad Extended Stay
TRINIDAD, CITY OF
TRINITY CENTER M.W.C. .
TRINITY CO. W.W. DIST #1
TRINITY KNOLLS MUTUAL WATER COMPANY
TRINITY VILLAGE MUTUAL WATER CO.
TULELAKE, CITY OF
Ukiah Valley Sanitation District
UKIAH, CITY OF
Ukiah City WWTP
Upper Russian River Water Agency
VALLEY FORD WATER ASSOCIATION
WADDINGTON W.W.
WAYSIDE GARDENS MOBILE HOME PARK
WEAVERVILLE C.S.D.
WEAVERVILLE S.D.
WEED, CITY OF
WEOTT C.S.D.
WENDELL WATER COMPANY (PUC)
WEST PARK PROPERTIES
WEST WATER COMPANY (PUC)
WESTERN MOBILE HOME PARK | Two wells, one above MCL, one below. Water from both sources is blended in tank so water delivered to homes is not above MCL. | 1
WESTHAVEN C.S.D.
Wildwood Campground
Willits City WWTP
WILLITS, CITY OF
WILLOW COUNTY WATER DISTRICT
WILLOW CREEK C.S.D.
WILLOWSIDE MUTUAL WATER COMPANY
WILSHIRE HEIGHTS MUTUAL WATER COMPANY
WINDSOR, TOWN OF | wells not potable due to arsenic, treatment methods under investigation. Alternative sources are in use (2019). | 1
Woods, The (Mendocino)
WOODSIDE RV PARK & CAMPGROUND
YREKA, CITY OF
YULUPA MUTUAL WATER COMPANY
6